- Security System Specifications LENEL

| Version | Date | Description of Revisions | Reason for Revisions |
| --- | --- | --- | --- |
| 1 | June 22, 2021 | General updates from consultant completed |  |

NOTE:

This Guideline does not override any governing codes, by-laws or municipal standards.  When conflict exists, the most stringent requirements will govern.

This is a CONTROLLED Document. Any documents appearing in paper form are not controlled and should be checked against the on-line file version prior to use.

Notice: This Document hardcopy must be used for reference purpose only.

The on-line copy is the current version of the document.

Any deviation from this document shall be approved by the Region Project Manager prior to proceeding.

Table of Contents

SECURITY REQUIREMENTS AND SPECIFICATIONS	5

1.	GENERAL REQUIREMENTS	6

1.1	Introduction	6

1.2	Overview	7

1.3	Applicable Standards	11

1.4	Software/System Configuration	11

1.5	Submittals	15

A.	General	15

B.	Shop Drawings:	15

C.	As-Built Documentation	16

1.6	Testing and Quality Assurance	18

1.7	Training	19

1.8	Network TCP/IP Coordination	21

1.9	Shop Drawings	21

2.	PRODUCTS	23

2.1	Security, Access Control and Intrusion Detection	23

2.2	Performance Criteria	24

2.3	Surveillance	24

2.4	Video Recording Requirements	28

2.5	Elevator Access Control Integration	30

2.6	Network and Video Cabling	35

2.7	Conduits, Pathways, Fittings, Cables and Miscellaneous Accessories	37

2.8	Parking Controls	38

2.9	Locksmithing and Door Hardware	40

2.10	Universal Washroom Requirements	41

3.	EXECUTION	42

3.1	Electrical Installation	42

3.2	Installation – Wires and Cables	42

3.3	Installation – Access Control System and Intrusion Detection System Devices	44

3.4	Installation – Enterprise Software Integration	50

3.5	Operation - General	50

3.6	Security Wiring Field Quality Control	53

3.7	Network Wiring Field Quality Control	53

3.8	Warranty	54

3.9	Close Out	56

3.10	Wiring Identification	56

3.11	Site Testing	56

APPENDICES	58

4.	LIST OF APPENDICES	59

4.1	Appendix A – Regional Security System Naming Convention Standards	60

4.2	Appendix B – Regional Approved Commissioning Form	61

4.3	Appendix C – Standardised Terminology	65

4.4	Appendix D – Standards Applicable to Regional Security Projects	77

4.5	Appendix E – Standardised Security Configurations	82

4.6	Appendix F – Procedure for Equipment Substitution	96

4.7	Appendix G – Standardised Abbreviations	103

4.8	Appendix H – Environmental Requirements	109

4.9	Appendix I – Access Control System Value Added Resellers	110

4.10	Appendix J – List of Approved Security Equipment	111

4.11	Appendix K – Approved Access Control Equipment	114

4.12	Appendix L – Approved Intrusion Detection Equipment	116

4.13	Appendix M – Approved Intercom Equipment	117

4.14	Appendix N – Approved Credential and Credential Reading Equipment	118

4.15	Appendix O – Miscellaneous Security Devices	119

4.16	Appendix P – Digital Video Management System	122

4.17	Appendix Q – Conduits, Fittings and Accessories	124

4.18	Appendix R – Cabling, Conductors and Miscellaneous Accessories	126

4.19	Appendix S – Parking Barriers	130

4.20	Appendix T – Locks	131

4.21	Appendix U – Universal Washroom	132

4.22	Appendix V – Labelling	133

4.23	Appendix W – Sample Graphic Alarm Map, Regional Layout and Icons	139

INDEX	141

left Intentionally Blank

- SECURITY REQUIREMENTS AND SPECIFICATIONS

- GENERAL REQUIREMENTS

  - Introduction

- This document provides all of the General Requirements applicable to any security related project undertaken by or on behalf of York Region.  These requirements are at all times subordinate to the requirements as defined in the Project Specifications and related documents, i.e., be it in the Specifications, the drawings or the Contract Documents.

- If there is any perceived lack of clarity or confusion, the Contractor has the responsibility to obtain clarification from York Region.

- The contractor is responsible for ensuring the reference documents, standards and specifications are the most recent version applicable to the current project.

- York Region will ensure that, as may occur, any modifications to its General Requirements are communicated to the Contractor.

- The Contractor shall use the General Requirements as provided in this document as a reference describing the design and installation procedures to be used for delivery of the project.  These procedures generally follow industry Best Practices applicable to Information Technology and Security Applications.

- This “General Specifications Document” consists of two inter-related sections:

  - General Requirements – which describes the overall design and functionality to be provided by the completed security system without reference to specific products; and

  - Appendices – which provide detailed reference to specific equipment, standards, protocols etc.

- Contractors are invited to advise York Region of any suggestions for improvements that could be made to the design or specifications.

- As technology evolves the Region will continue to upgrade software and hardware in order to ensure the highest levels of security and reliability for all of its properties and facilities.  Hence the contractors working on new projects are responsible to validate the versions of software, firmware and hardware currently in service and to validate the compatibility of any new installations with the existing installations.

- All equipment installed during the execution of any security projects shall be acquired through manufacturer approved dealers and installed by factory trained and approved technicians.  Approved sources for the primary items of equipment are identified in the Appendices I, J, K and L.

- The contents of this document are to be considered confidential and remain the property of York Region and prior permission shall be obtained for any use or copying of the contents which is unrelated to work which is being undertaken for York Region.

  - Overview

- The Regional Municipality of York (York Region) is committed to operating a single security system for the all the Region’s properties.  The state-of-the-art system is configured using industry standard products as specified here.  The implementation is currently in operation at many locations but will continue to be deployed at additional locations as opportunities arise.

- The Regional security system has 3 distinct components and these components are described further below.  The components are designed to monitor and control:

  - Access Control (AC) using personal access cards;

  - Intrusion Detection (ID) using multiple sensors and detectors;

  - Closed Circuit Television (CCTV) cameras used to monitor key locations;

  - Intercoms which allow for those wishing access at a gate or door to communicate with the operations centre; and

  - Panic alarms which are sometimes inaccurately referred to as “Life Safety” devices and which are generally located in areas where “disruptions” may occur, e.g., reception areas, judicial services, social services, health services, etc.  Some of the panic alarm buttons are wired and others are wireless.

- The independent, commercial products are integrated so that the system operators are able to control and manage all the security functions enumerated above from the single user interface which is connected only to the Access Control System.  The diagram below (Figure 1) is intended to provided a high-level overview of how the key components of the Region’s security system are interconnected.

- Figure 2, below shows how York Region’s remote sites are interconnected with the Main Regional Control Centre.  Key aspects are that the security system at each site functions locally but all activities and exceptions are communicated to the primary equipment which is located at the Main Regional Control Centre.  The architecture is fully scalable and is the same at all sites as appropriate, e.g., the water treatment facilities use SCADA displays for local alarm monitoring which are different than at other sites.

Figure 1: Overview of York Region’s Security System Architecture

Figure 2: Architecture for the Sites Connected to the Main Regional Control Centre

- The Access Control System and also its User Interface are based on a single, previously approved, security system, for which details can be found in Appendices J and K.  The door hardware is controlled by the most recent available interfaces available from the same single manufacturer or supplier.  Power supplies are all provided by a single manufacturer, who must be approved by the security system manufacturer.  More details regarding these devices may be found in Appendix J.

- The integration of the Access Control and the Intrusion Detection aspects of the security system shall be achieved via the network for full control of both components via the server as well as at a local level for seamless offline operation.

- The CCTV System shall be based on a standard, commercial, digital video management system as detailed in Appendix P.

- The Contractor shall work with York Region on the technical design of the proposed system or contract work, clarification of technical requirements and shall provide a full set of Technical Shop Drawings for approval before proceeding to installation.  The Technical Shop Drawings shall include, but not be limited to, network connectivity diagrams, high level riser diagram(s), system riser diagram(s), vertical and horizontal wiring diagrams, typical and site specific device termination/wiring schematic(s) and diagrams, hardware DIP Switch setting configuration(s), device landing schedule(s), system integration wiring diagrams, intrusion detection point schedule(s), tub/enclosure layout diagram(s), electrical connections and wiring diagrams, explanation of the sequence of operation, integration techniques and operational scenarios.  The Contractor shall adhere to the Region’s conventions including the allocation of sequential addresses commencing from “1” and avoidance of any reserved addresses.  The Contractor shall clearly identify any dependencies which are not included in these Drawings, such as wall space, electrical requirements, air conditioning.

- In addition to the foregoing Shop Drawings, the Contractor shall provide addressing charts, product specifications, and cut-sheets, and other relevant information, required by York Region to complete the full evaluation of the design and to provide for the contractor’s installation.

- Following approval by York Region, the Contractor shall deliver one hard copy and one electronic copy of the Technical Shop Drawings to the security system installer for review and comment.  The hard copy of these documents shall be printed so that they may be readily read and marked up as may be required.

- The electronic documents shall be delivered both in editable form, i.e., AutoCAD or Word and also in PDF formats.

- The Contractor shall at all times certify that all the electronic documents and the media which are being submitted have all been checked for all forms of malware prior to their submission for any purpose to any other party using any means of transmission.

- The comments made by the security system installer are to be shared with York Region so that it is aware of any concerns which may have been expressed by the installer.  York Region shall approve or, as may be appropriate, justify adoption of the original design or a modified variation before any changes are incorporated.  The costs and schedule impact of any such changes shall be clearly identified in these documents.

- The Contractor shall be fully responsible for the work completed by its employees as well as its sub-contractors, including the security system installers, electrical contractor, locksmith and door hardware subcontractors.  The Contractor shall employ the installation services of one of the Region’s approved security system installers, as listed in Appendix I; to perform the installation and configuration of the security system.

- The installation and termination of all required conduit, cabling, network equipment, communication lines and devices, security devices and head end equipment shall be completed by a pre-qualified security system installer (See Appendix I).  All necessary cable, conduit, fittings, and other general installation hardware shall be specified by the Contractor and supplied and installed by the security system installer or by other specialist sub contractors retained by the security system installer, e.g., network installers or electricians.

- The Contractor shall be responsible for supplying the system equipment, licencing, and hardware in accordance with the Contract Documents, including Specifications and Drawings provided by the Region.  The Contractor shall be responsible for the final design, supply, installation, configuration, testing and commissioning of the fully operational system to the satisfaction of the Region.

- Where an item is shown on the Drawings and is specified in this Specification, such item shall conform to the requirements of this Specification Section.

- The Contractor and all others working for the Contractor shall conform to all of the requirements of this Specification, including as may be appropriate, all of the related appendices.

- The Contractor shall provide design (shop) drawings prior to the execution of the work, identifying all physical security devices which are to be installed at each field location in accordance with the requirements in the Contract Documents as provided by York Region and as specified in Appendices E, J, K, L, M, N and O.

- All work undertaken in this project shall conform to the standards and practices identified in these security specifications and as noted in Appendix D.

- As required, the Contractor shall submit the necessary number of working drawings and specifications to any applicable authority for examination and approval prior to commencement of work.  Any changes required by the examining authority shall be reviewed and approved by York Region.

- Carry out all changes and alterations required by an authorized inspector of the ESA and any other authority having jurisdiction without delay to the progress of the Work.  All such changes shall be reviewed and approved by York Region.

- The Contractor shall fully train the Region’s personnel (and contractors if applicable) to operate and to perform routine maintenance on the systems and equipment which is installed under the current contract.

- The Contractor shall provide all warranty services for facility security system for a period of two (2) years from the date of Total Performance of the Work, and shall provide all necessary material required to replace any defective products during this period.  The warranty period shall restart from the date of the completion of such replacement.

- Details of the Pre-Qualified Value-Added Resellers and Installers may be found in Appendix I.

  - Applicable Standards

- All work performed for York Region must be inspected and approved prior to being commissioned.  Such work must be compliant with all of the applicable Standards.  Some of these Standards may be found in Appendix D.  It is the responsibility of the contractor to ensure that the Standards being applied to any project are:

  - The most current version of the Standard or Code; and

  - Those applicable in the specific project and in the specific jurisdiction.

  - Software/System Configuration

- The Security System installed as part of this Contract or any modifications to the existing installation shall be reflected in the existing security system database.  All programming and configuration for the work under this Contract must be consistent with the existing programming to guarantee consistent functionality of the system and all of its components across the Region.

- The Contractor is only responsible for the work related to this Contract and shall NOT adjust or alter the existing configuration for any other facilities within the system without written authorization from the Region.  The Contractor shall NOT alter, modify, delete or interfere in any way with any settings, configuration or variables that may affect the functionality of the existing facilities, systems or their components without prior written authorization from the Region.

- The installed Security Access Control system must be configured to meet all existing Regional standards (Security, Operational, IT).  The Contractor shall be responsible for identifying the requirements, developing a custom solution to meet those requirements, and presenting available options in the form of an implementation plan to the Region for approval before implementing the proposed solution.

- All software licencing must be detailed, supplied and installed to operate the security solution.  The Contractor shall supply and install all of the necessary proprietary integration licences, card reader licences and workstation licences, as may be required.  It is the Contractor’s responsibility to quantify and provide the number of licences required based on the Drawings and Specifications provided in the Contract Documents.  All costs associated with provision of the required licences shall be included in the Contract Price including any modifications to the Contract Price.

- The Contractor shall work with the Region’s IT department to perform application or database server programming and configuration and network device security penetration testing.  The contractor shall supply copies of all network device specifications and data sheets to IT when requested in preparation for the penetration testing.  All work requiring access to the database and/or application servers must be coordinated with the Region a minimum of one week in advance.

- All changes to the network configuration and network attached devices must be approved by the ITS department to ensure that the network complies with ITS’s “penetration” resistance requirements.  It is noted that IT maintains a list of approved devices which may therefore not require individual testing.  In the event that penetration testing is required, the costs of the testing incurred by the Contractor, and of any remediation which may be required by IT, will be borne by the Region if the deficiency is encountered after the award of contract.

- All server, network, and other requirements shall be coordinated with the Regional IT Services department and validated by the security system manufacturer prior to installation.  All servers and network switches shall be provided by the Region unless otherwise specified in the Contract Documents.

- The software and/or system deployment and configuration shall be overseen and validated by the Regional representative(s) from the Capital Delivery Coordinator department.  The Contractor shall use manufacturer provided software applications to program, configure and test the system.  No configuration shall be completed utilizing any client applications on the client servers.

- There shall be a single, integrated, Audit Trail log which records all of the actions and activities for the entire site.  The integration of the activities at each site shall be similar, subject only to the configuration of the site, and shall include:

  - Local date and time (using Canadian - ISO style and 24 hour clock);

  - All access card activities including name, action granted or denied and reason;

  - Logging in and out of operators;

  - Schedule activations and deactivations;

  - Trouble and alarm reports;

  - All failures, arming and disarming of systems; and

  - System resets and restarts.

- The intrusion detection system at each Facility (or group of buildings) must be armed by using a card swipe on the card reader on the secure side of the door followed by pressing a button which is labelled for this purpose.  The intrusion detection system must disarm automatically when access is granted at a perimeter door, i.e., an access which is granted, at a perimeter door will disarm the intrusion detection system unless otherwise specified.  Note that the door does not have to be opened for the alarm system to be disarmed.  The intrusion detection system shall not permit arming until all intrusion points are “fault free”, i.e., closed.  This arming process may proceed if trouble alarms, which generally are not operational, are present.  All relevant information related to the current status of the area shall be displayed on the local intrusion detection system keypad(s).  The same information shall also be displayed by means of dynamic icons on the local and the central, access control interface Alarm Monitoring software client interactive map.  Integration between the access control hardware, the access control software and the intrusion system must be seamless in both online and offline modes.  The contractor shall create custom alarms for each facility which shall properly display any intrusion events using the access control Alarm Monitoring application.

- The intrusion detection system Alarm Keypads shall display the name of the facility and the nature of any faults in the system but shall not be used for “Arming” the system, “Disarming” the system or clearing any faults.  All the keypads in each facility shall also annunciate any active alarms occurring in that facility using its internal sounder, e.g., intrusion alarms, panic alarm, system failure.

- Arming shall be implemented locally by a valid card swipe on an adjacent, dedicated, internal card reader followed by a button press or, alternatively, through the access control system Interactive Map utilizing dynamic icons.

- Disarming shall be performed locally by a valid card swipe on any of the external, perimeter readers or, alternatively, through the access control Interactive Map utilizing dynamic icons.

- The intrusion detection system shall allow persons to exit from the facility without triggering an event until the system is fully armed after the exit delay time.  The system shall alarm instantaneously when any intrusion zone is faulted while the system is in the armed state and shall record details in the Audit Trail log.  All intrusion alarms shall be annunciated:

  - Locally on all the keypad(s) at the corresponding Facility;

  - On the local access control system graphic map(s) where available;

  - Remotely on the access control system Alarm Monitor client application;

  - To the 3rd party Central Monitoring Station; and

  - To the SCADA Control Panel for ENV OMM facilities.

- The Contractor shall create or update a graphical map interface for the system reflecting any work performed under the current contract, making it the same or similar in appearance and functionality to the existing graphical maps (see Appendix W: “Graphic Maps").  The graphical map interface shall be implemented as a multilayer hierarchy with the highest level or main map displayed as a map of York Region identifying all the municipal boundaries.

- The Regional facilities shall be represented on the display using distinct icons depicting corporate, environmental, transportation, paramedic and other departments (see Appendix W).  Each facility shall be represented by the applicable architectural floor plan, (multilayered, if necessary), to identify the areas, floors and buildings.  The facility graphical map shall be created by the Contractor from the CAD or PDF files which are provided by the Region, in a resolution which displays properly on a typical 24” display configured at 1920 x 1080 PPI resolution unless otherwise specified.  Pixilated, blurred and/or illegible maps shall not be accepted.  See Appendix W: “Graphic Maps”, for further information.

- The graphical interface shall show all field devices together with their associated status dispositions.  Typical status options shall include but are not limited to Armed, Disarmed, Normal, Alarmed, Forced, Held Open, Locked, Unlocked, Tamper, Faulted, Active, On schedule, Offline, AC Fail, Battery Trouble, etc. (see Appendix C for meaning of foregoing terms).  All required status symbols are already available and may be reused for this project.  Some of the symbols developed specifically for York Region are shown in Appendix W: “Graphic Maps”.

- Each facility’s graphical map shall contain a displayed control /status panel allowing direct control with functions, such as Arm, Disarm, Door control operations, intrusion area operations, map navigation, etc., and at all times displaying the real-time status of the facility, such as Armed/Disarmed Status, Ready to Arm Status, Intrusion Alarm Status, System Components Status etc. (see Appendix C for meaning of terms).  The Contractor shall use the existing custom dynamic icons to populate the graphical interface or, if necessary, create additional icons.  The existing custom icons will be provided to the contractor on request.

- Whenever a panic alarm is activated, the local graphic map display and the central graphic map display (as may be available) will immediately both be updated to identify the location of the active alarm by showing a flashing red icon at the alarm location and display a text message on the keypad which will also be sounding.  The screen will have an icon “Panic Clear” which both clears the map display and also silences the keypad.

- The Contractor shall create new and update existing Schedules (Time Zones), Access Levels and Monitor Zones (to enable remote monitoring by system administrators), as may be required for each contract.  The Region shall provide the Contractor with the initial configurations for these options.

- All system components shall be configured using the Regional Security System Naming Conventions Standards as outlined in Appendix A.  Naming conventions shall be consistent throughout the system.

- All security panels shall report AC Fail, AC Restore, Battery Trouble and enclosure tamper events to the Access Control System Software by using the Alarm Monitoring application and this information shall be displayed on the graphical maps by means of the corresponding dynamic icons.

- Batteries included in any panels or modules which are supplied or installed in the course of the Contract, shall be labelled identifying the date of initial deployment using the ISO 8601 format, i.e., YYYYMMDD or YYYY-MM-DD.

- The Contractor shall update all system hardware components with the latest manufacturer approved firmware versions prior to final commissioning.  The Contractor shall ensure that any firmware updates are fully compatible with the existing software releases prior to performing such upgrades.  Where firmware versions are indicated by the manufacturer on the devices or in the devices, updates performed by the Contractor shall be reflected by modifying the original labelling so as to show the installed version or release of the firmware.

  - Submittals

  - General

- All submittals to the Region will be reviewed by the Region and must be accepted by the Region before any construction is permitted.

- Submissions shall be made in accordance with the schedule developed and approved for each project and shall comply with all of the requirements as stated in this document and in the Contract Documents.

- All submissions shall be in English and spell checked in accordance with normal Canadian spelling and grammatical practices.  The text documents shall use Times Roman font in 11 point as the body font with a minimum of single line spacing.

- As described in Section 1.2 the submission shall be provided in at least one hard copy and one electronic copy.  The former shall be printed single sided and suitably bound and indexed on 8.5 x 11 ins.  Drawings shall be printed in a size to be agreed to between the parties and provided with a suitable cover page and index page.  The electronic copy shall be provided both in an editable format using Microsoft Word for text and AutoCAD for drawings and also in Adobe PDF.  These files may be transferred via a secure link or on a portable storage medium.  The Contractor is responsible to certify that all of the electronic files are free of any malware and the files shall have no electronic locks, encryption or restrictions.

- York Region shall review the documents and provide comments to the Contractor indicating in particular if the Contractor may or may not proceed with the project and if a modified submittal is required.  These comments shall be provided to the Contractor within 15 working days, unless an alternative schedule is agreed to by all parties.

- York Region and its agents shall be the final arbiter with regard to the suitability of the submissions.

  - Shop Drawings:

- Prior to the start of construction, the Contractor shall submit a complete set of:

  - all relevant technical documentation, and

  - technical shop drawings and specifications

for approval by the Region and also for review by the Security Installation Contractor prior to the implementation phase of the project.

- The Contractor shall provide one full hardcopy and one digital copy of shop drawings (see Section 1.5.1 and Appendix D) which shall cover the entire scope of the Work as defined by the Contract Documents, including but not limited to:

- System riser diagram(s)

- System layout/floorplan

- Network connectivity diagrams

- Vertical and horizontal wiring diagrams

- Typical and site-specific termination/wiring schematic(s) and diagrams

- DIP Switch and similar configurations

- Device landing schedule(s)

- System integration schematic(s) and wiring diagrams

- Intrusion detection point schedule(s)

- Tub/enclosure layout diagram(s)

- Electrical connections and wiring diagrams

- Explanation of the sequence of operation

- Integration techniques and operational scenarios

- Addressing charts

- Product specifications and cut-sheets

- Complete Bill of Materials

- Proposed testing and acceptance activities

- Other relevant information required for the installation

  - As-Built Documentation

- The as-built drawings, documents and materials as described here shall be submitted no later than 15 Working Days after the substantial completion of Work, i.e., after the commissioning of the system has been completed and any identified deficiencies have been resolved.

- All as-built documentation must use the Region defined naming convention for all system components and must be consistent with the naming convention used in the software.

- The Contractor shall submit detailed documentation describing the entire scope and extent of the Work which has been performed in accordance with the Contract Documents, in compliance with the requirements identified in Appendix D.  The requirement is that this documentation shall be sufficient for “a person knowledgeable in the industry and familiar with the technology to have the ability to perform the work described in the Contract Documents without the need for further instruction”.  These documents shall include, as may be appropriate, some or all of the following but are not limited to:

  - As-built drawings, documents and materials: In conformity with the requirements noted in Appendix D, the documentation shall cover the entire scope of work, including but not limited to the items listed below and detailed commissioning documentation, as well as other relevant information, e.g., firmware versions, warranty details.  In practice the Contractor is expected to resubmit the shop drawings, which were submitted earlier, with the incorporation of the modifications to reflect the actual work which has been completed.

- System riser diagram(s)

- System layout/floorplan

- Network connectivity diagrams

- Vertical and horizontal wiring diagrams

- Typical and site-specific termination/wiring schematic(s) and diagrams

- DIP Switch and similar configurations

- Device landing schedule(s)

- System integration schematic(s) and wiring diagrams

- Intrusion detection point schedule(s)

- Tub/enclosure layout diagram(s)

- Electrical connections and wiring diagrams

- Explanation of the sequence of operation

- Integration techniques and operational scenarios

- Addressing charts

- Product specifications and cut-sheets

- Complete Bill of Material

- Documents recorded during the testing and acceptance activities

- Other relevant information

  - One additional hard copy of the as-built drawings with all relevant drawings and documentation shall be provided by the Contractor and stored on-site inside or near to the main system enclosure along with warranty/contact information.

  - All technical notes, software scripts, firmware details and other documentation covering the IT portion of the Work covered under this Contract.  All configuration modifications and configuration backup files shall be documented as a part of the as-built package.

  - Lists of all passwords, keywords, serial numbers, licences and/or configurations that are encountered during the installation and configuration of the system.

  - Complete set of manufacturers’ installation manuals, maintenance manuals and specifications for all system software and hardware components by make and model.  This information shall include comprehensive, descriptive data sheets, brochures, installation, and technical manuals for all systems and equipment forming part of the contract.  The manuals shall include operational and schematic diagrams for the System and all related components.

  - Detailed commissioning documentation in the format approved by the Region (see Appendix B), populated with all relevant information and worksheets identifying all testing and commissioning procedures which were undertaken.  The commissioning documentation must be completed by the Contractor and signed by the Regional representative.  An example of the Region approved commissioning form is presented in Appendix B.

  - Theory of Operation – system outline and overview.

  - Operational manuals explaining the system operator’s available features, functions and capabilities.

  - System administration manuals including operational and maintenance requirements and procedures associated with the proposed solution.  Description of administrative functions required to supervise and manage the integrated system(s).

  - Full schedule of maintenance which is to be carried out on each system component during the warranty period of 24 months after the date of Total Performance of the Work and for the entire lifetime of the system and its components.

  - The Contractor shall commit to the Region that the Contractor will meet the Region’s requirements for response time and return to service time in regard to any service calls made during the Warranty period and that suitable spare parts will be readily available to meet those commitments.

  - The contractor shall propose an inventory of spare parts which the Region may wish to acquire for the system following expiry of the Warranty period.

  - Testing and Quality Assurance

- The Contractor shall ensure that, upon completion of the contract, all hardware and software components are functioning as intended within the Region’s IT and the security network environments.

- At the discretion of the Region, final acceptance testing shall be carried out at any or all of the following defined levels:

  - per point basis;

  - per system component basis;

  - per software function basis; and

  - per total system basis.

- The Contractor shall document, test and verify the proper installation and functionality of the system and all of its components including integration to the systems described in this Section, application and database integration as well as online and offline operation.  Upon request, these functionalities shall be demonstrated to the satisfaction of the Region which shall be performed without extra cost to the Region.

- The Contractor shall inspect all installed devices and equipment to ensure that all of these devices will achieve the intended system functionality.  Any devices which are not capable of fulfilling the required system functionality shall be documented to the Region in writing.  Any corrective measures which are required shall be approved by the Region and the Contractor.  The costs for any modifications are to be borne by the Contractor unless the equipment configuration was selected by the Region.

- The Contractor shall test all field devices and system components which are configurable or adjustable to ensure that they achieve optimal performance and fulfill the performance requirements as installed.  All configurable settings must be approved by the Region prior to installation and shall be documented for the Region.  Upon request, this shall be demonstrated to the satisfaction of the Region without extra cost to the Region.

- All tests shall be performed to the satisfaction of the Region and, if any tests are repeated and then achieve different results, the Region has the option of requesting device replacement.  If any adjustments are made in order to achieve the required test results, the Region or the Contractor shall identify if other tests need to be repeated to ensure that the adjustment does not prejudice any other test results.  All such retesting and adjustments shall be performed without extra costs to the Region.

- Once the Contractor has established that the System is operating as required, on-site commissioning shall be scheduled with the Regional representative(s).  The contractor shall demonstrate to the satisfaction of the Region that the system and all of its components are functioning, as intended by the approved design.  This approval process shall be performed in 2 phases:

  - A pre-commissioning demonstration with the Region’s Security System Administrator who may be reached at (905) 830-4444 ext.76900 and:

  - A final commissioning with the Region’s Capital Delivery Project Coordinator.

- The testing and commissioning shall be completed and accepted both by the on-site Regional Project Coordinator and by the remote Regional Security and York Region System Administrators.  It is the responsibility of the Contractor to arrange and carry out commissioning sessions with the Region and to provide all parties with suitable records of the commissioning and minutes of the activities.

- In the event that the testing and commissioning activities do not meet with the approval of any of the Regional representatives, the Contractor is required to address the matters that led to the rejection of the system.  Such alterations and repeating of the test and commissioning processes, in part or in whole, shall be performed expeditiously and without extra charges to the Region.

- The Contractor shall assist the Region in configuring, and/or reconfiguring, and populating, and/or repopulating all System related databases.  As may be required, the Contractor shall also assist with any modifications which may be required to the existing integrations, configuring and/or reconfiguring all the system parameters to the Region’s satisfaction.  All the procedures and activities required to accomplish such changes shall be fully documented and shall, as may be applicable, follow existing procedures.

- The Contractor’s assistance shall continue until initial configurations and integrations are complete and functional, and/or until all affected systems are working to the Region’s satisfaction and the related documentation has been accepted by the Region.  In the event of any matters arising during the 12 months immediately following the acceptance of the system by the Region, the Contractor shall provide suitable assistance to achieve resolution under the terms of the Warranty.

- The assistance, referenced in the above paragraphs, shall be provided by a single technician working physically side by side with the Region’s representative(s) assisting and instructing the Region’s representative(s) step by step in configuring system parameters and integration configurations to the systems outlined in the Contract Documents.

  - Training

- The purpose of the training is to allow the local and the Regional staff to safely and reliably:

  - Perform all routine operations and maintenance functions required for the systems;

  - Make minor changes to the system configurations;

  - Address any intrusions, access card management issues, emergencies, accommodate visitors, manage issues related to parking and deliveries; and

  - Recognise when more expert advice is required and to identify the nature of that requirement.

- Training of the Regional staff shall be provided by Contractor staff familiar with the project and equipment and experienced in delivering such training courses in English.  If the training is considered inadequate by the Region, it shall be repeated without extra charges to the Region.

- All necessary supplies and documentation for the training course shall be supplied by the Contractor.  The Region shall provide a location with basic audio-visual equipment, i.e., a screen, tables, chairs and internet accessibility.  Other equipment and network access can be requested but might not be provided by the Region.

- The training program shall provide suitable training for those at the Region responsible for operation, the administration and the supporting of the “security systems”.  The scope of the training shall cover the entire scope of work defined by the Contract Documents as well as its interaction with previously existing systems.

- The Contractor shall provide a detailed description and syllabus of the training program to the Region for review at least 2 weeks ahead of the proposed training session.  This description shall identify:

  - The intended audience for the upcoming training session, i.e., system operators, system administrators or support staff;

  - The material to be presented;

  - The supplies being provided by the Contractor;

  - Any supplies (other than the training room) to be provided by the Region; and

  - The anticipated duration of the training program.

- The Region shall review the proposed training program and provide comments to the Contractor.  If the comments are significant the Region may elect, without incurring any extra charges to delay the training program and to undertake a further review of the edited training program.

- The Region shall identify the number of individuals anticipated at the planned training session at least 1 week prior to the start of the training session.

- Training documentation shall be developed by the Contractor in adequate quantities to satisfy the requirements of the training; and shall be submitted by the Contractor for future reference by the Region in printed and digital formats (see Appendix D).  At the discretion of the Region, the training session may be recorded.  Such a recording shall be used only by the Region and its employees for internal training purposes, e.g., additional employees.

- Training may not take place using the Region’s live system but the Contractor may, by mutual agreement between the Contractor and the Region, use the Region’s live system to show the reality of a “live system”.

- The Contractor shall ask the attendees partaking in the training session to complete an evaluation of the training program to help with improvements to future training sessions.  The results of this survey shall be provided to the Region.

  - Network TCP/IP Coordination

- The Region’s Project Manager will coordinate the installation of any required network system components or modifications with ITS (Information Technology Services) Department and the appropriate BSA (Business System Analyst) at the Site.  Such changes may be required to allow for communications between the new security installation and the database server(s) which are located at Region’s Central Monitoring Station so as to provide the requisite tie in and commissioning of the security system.

- The Contractor is reminded that all equipment which is being installed to the network must comply with ITS’s penetration approval requirements (see Section 1.4.6).

- If local, wired, IT Wide Area Network infrastructure is not present on a site, Wireless network equipment shall be used.  York Region ITS will supply the contractor with the pre-configured Wireless Modem and network switch as well as specific installation instructions.

- The Contractor shall install all required conduits and junction boxes as well as the exterior antenna for the Wireless equipment, in a location which has been identified by ITS to provide suitable network performance for this application.  If required, the Contractor shall provide such additional infrastructure as may be required to ensure that the complete communications system performs in accordance with the design.  Note that, in accordance with Code requirements, conductive data and high power cables (120 V or higher) cannot be placed in the same conduits.

- The wide area network data switch shall be located within the access control system cabinet.  Both the modem and the data switch shall be powered from the UPS power supplies being used by the access control system.

  - Shop Drawings

- Submit shop drawings showing the proposed location of all equipment to be installed under this Contract.

- Shop drawings submission shall include, as may be appropriate, some or all of the following:

- System riser diagram(s)

- System layout/floorplan

- Network connectivity diagrams

- Vertical and horizontal wiring diagrams

- Typical and site-specific termination/wiring schematic(s) and diagrams

- DIP Switch and similar configurations

- Device landing schedule(s)

- System integration schematic(s) and wiring diagrams

- Intrusion detection point schedule(s)

- Tub/enclosure layout diagram(s)

- Electrical connections and wiring diagrams

- Explanation of the sequence of operation

- Integration techniques and operational scenarios

- Addressing charts

- Product specifications and cut-sheets

- Complete Bill of Materia

- Description of test methodology

- Other relevant information required for the installation

- Additional Shop Drawing Requirements:

  - For devices containing DIP switches, jumpers or programming keypads include with the shop drawings, as appropriate:

- Functional description.

- Performance data.

- Physical, electrical and environmental requirements.

- Location drawing.

- Equipment descriptive literature.

- Wiring details.

  - For programmable equipment, communication links and networks, submit a Bill of Materials.  Include the hardware documentation with the Bill of Materials.

- For hardware items include and clearly identify:  Description, make, model, part number and serial number (once this available).

- For documentation include:  Title, version, date and publisher for each item.

  - For Programmable Hardware Equipment include:

- Product description for each item including:

- Wiring and installation instructions.

- Functional description.

- Performance data.

- Physical, electrical and environmental requirements.

- Adapters and controllers.

- Equipment layout drawings showing location of hardware, boards, jacks, cables and terminals.

- Related field tag numbers and wire numbers, module tag assignment, rack module assignment, and terminal numbers.

- Location, identifier and pin assignment of plugs, jacks, and cables.

- Switch settings and addresses, firmware.

- Interconnection Diagrams including wiring, cables, jacks between internal and external components, power supplies, processors, communications modules, racks, input/output modules and peripherals.  Label terminals, jacks and pins.  Show settings for jumpers and switches.  Show address for each hardware module and point.

- Any backup or other maintenance requirements.

- Listing (hard and digital copies) of all programming details.

- The review of shop drawings shall only be in reference to general design.  The review of the shop drawings shall not, in any way, relieve the Contractor of responsibility for errors, omissions or physical interference, or from the necessity of furnishing such work and materials as may be required for the completion of the work at any time prior to formal acceptance.  The Contractor shall be cognisant that the shop drawings may require resubmission before the contractor may proceed to the next phase of the project (see submission of Shop Drawings under General Requirements).

- PRODUCTS

  - Security, Access Control and Intrusion Detection

- Because of the deployment of existing devices which have all been designed to provide a uniform security solution for all properties belonging to York Region, there are pre-approved devices and solutions which shall be used wherever possible.

- These pre approved security devices are listed in the Appendices J, K, L, M, N and O.

- Appendix J	List of Approved Security Equipment

- Appendix K	Approved Access Control Equipment

- Appendix L	Approved Intrusion Detection Equipment

- Appendix M	Intercom Equipment

- Appendix N	Approved Card Reader Equipment

- Appendix O	Miscellaneous Security Devices

- Typical installation configurations in which these devices are used may be found in the sample “assembly drawings” which are shown in Appendix E “Standardized Security Configurations”.

- The Contractor shall ensure that all supplied systems which are to be deployed are compatible with the existing security installation.  Hence the general industry guideline of using the most recent versions of software, firmware and hardware may lead to unsatisfactory performance due to incompatibility.  It should be noted that the existing installation may not have been updated to the latest versions because of prior, known incompatibilities.  The contractor is responsible to validate all such equipment and ensure full compatibility between newly supplied equipment and the already installed components.  Any proposed firmware or software updates must therefore be reviewed with the Region before any updates are undertaken.  If any modifications or upgrades are required, these changes must be included in the project budget and identified in the proposal.

- The contractor may request that the Region consider use of devices other than those pre-approved by the Region.  The procedure and the form to be submitted when requesting such a substitution is set forth in Appendix F “Procedure for Equipment Substitution”.  It should be noted that the decision of the Region in regard to any such request is final.

- The use of any equipment which is not approved by the Region shall constitute a Breach of Contract and grounds for terminating the Contract in progress and lead to an Action to complete the contract in accordance with the approved design as well as consequential damages.

  - Performance Criteria

- Contractors shall recognise that the purpose of installing any Security System is to ensure that intruders cannot enter and that any attempt to bypass or otherwise defeat the hardening which has also been installed in order to deter intruders must successfully report all details of this attempt.

- The Region is therefore adopting suitable criteria which they will use to determine the effectiveness of the Security Systems.

- The Probability Of Detection (POD) is a measure which is described in Appendix C -- Standardised Abbreviations and, as its title implies, recognizes that some Security Systems do not detect every attempt at compromise.  The Region expects however that the POD shall meet or exceed 97% with suitable information being provided in a timely manner to the security staff for them to investigate.

- The corollary to an effective detection system is that the system must have a very low False Alarm Rate (FAR).  It is well known in the industry that false alarms are a major cause of the failure to detect intrusion attempts.  When an alarm is reported and the security patrol determines that this was caused by “acceptable events” it is either classified as a false alarm or as a “nuisance alarm”.  Both of these situations generate distrust in the alarm system ultimately leading to the failure of responders to pay attention to alarms.  (See further discussion in Appendix C – Standardised Terminology.)

- The Region will not accept a false alarm rate which exceeds 2% i.e., no more than two out of every hundred reported alarms may be classified as a false alarm or as a nuisance alarm.

  - Surveillance

- Because of the existing deployment of devices which have been designed to provide a uniform surveillance solution for all properties belonging to York Region, there are pre-approved devices and solutions which should be used wherever possible.

- Surveillance cameras shall be installed so that they can observe locations which would otherwise require regular security guard patrols.  The images stored on the DVMS system must be of sufficient quality to fulfill the expectations of the designer.  There are many factors which affect the quality of the image and these need to be clearly defined for a satisfactory outcome of the Contract.  The following identifies a number of the key factors which may need consideration:

    - Stability

If a surveillance camera is mounted on an unstable base, the image may be very hard to interpret.  This applies much more to outdoor cameras where the camera may be mounted on a pole or a building roof and wind plays a major role.  Indoors there can be issues related to a wall in which there is a frequently used door which may slam shut with vibrations affecting the stability of the camera.  It is clear that a minor vibration on a wide-angle lens may be barely perceived at an image distance of 15 m (50 ft) but if the same installation is used with a telephoto lens looking at an image distance of 1,500 m (~5,000 ft) the same deflection caused by the vibration will cause 100 times the distortion of the image.  There are different forms of stabilization which can reduce the impact of any vibration transmitted to the images if the source of the vibration cannot be eliminated.

    - Pixels on Target

The effectiveness of an image by which to identify an intruder when using a surveillance camera is determined by the number of image pixels used to provide the image of the topic of interest.  In security surveillance applications this is usually defined in terms of a requirement, such as the resolution of the viewing screen, the resolution of the camera, the size of the screen, the height of the “target human intruder” and the minimum acceptable image size, e.g., “the minimum height of the human who is 1.8 m (~6 ft) at a distance of 30 m (~100ft) shall be 7.5 cms (~3 ins) on a 21 inch screen.  This may be calculated for a particular configuration such as an 18 mm lens with a 15 µ pixel pitch to have a “Detection” range of 537 m (~1,750 ft), a “Recognition” range of 134 m (~440 ft) and an “Identification” range of 84 m (~275 ft).

    - Recognition vs Detection

The camera designer must answer the question as to the purpose of any surveillance camera installation.  The criteria for an acceptable surveillance image are often based, at least in part, Johnson’s Criteria.  Generally, the purpose of surveillance in a security setting may be defined as one of the following:

- Detection: an object is present – 2 pixels on target.

- Recognition: discern the type of object, a human versus a vehicle – 8 pixels on target.

- Identification: discern specific objects, a man versus a woman, a car model – 12.8 pixels on target.

The above examples are simplified and ignore the image quality which is affected by lighting, contrast and other issues such as moving trees which can provide additional challenges.

    - CIF vs Frame Rate

When recording images there are a number of terms which are used and which should be understood;

- CIF is Common Intermediate Format (360 x 240 pixels) and is a common format used for recording digital images to be played back in any standard format.

- 4CIF is an enhanced quality image over CIF and provides data at 704 x 480 pixels.

- Frames per second reflects the rate at which images are refreshed and is the term which was widely used with Analog(ue) Cameras which are now no longer current.  Common values are 30 or 60 fps (the latter of consequence with high-speed action).  This is of course the speed at which the older film technology moved the “celluloid” through the projector.

    - Illumination and Shadows

Illumination by artificial sources always generates shadows in the same place whereas illumination by the sun or even the moon causes shadows which vary by time of day and also by season.  From a security perspective the shadows are a potential hiding place for any malfeasant.  Hence great care is required to ensure that shading hiding places are minimised as is the basis of CPTED.

    - Infra Red

Many security cameras are now available with integrated IR illuminators which allow the cameras to “see in the dark”.  Infra red illuminators are harmless to humans and animals and are invisible without technological aids so that such surveillance can be considered “covert”.  The images provided by these cameras are monochrome (generally appearing as black and white) as the lighting source is a single frequency.

    - Thermal Cameras

Thermal cameras, which are sometimes incorrectly referred to as infra red cameras because they detect “heat” (which is related to infra red waves), will display images based on the heat signature of any item in the field of view which differs from the background.  These cameras can provide very effective imaging with no artificial light during any time of day and are oblivious to the shadows or glare caused by natural or artificial lighting.  Generally, because of optical considerations, zoom lenses are not available for thermal cameras.  One popular option is to co-locate a thermal camera with an optical camera thereby providing versatile and reliable imaging at any time of day.

    - Direct Sunlight

The glare caused by direct or reflected sunlight will cause optical camera images to “be blinded” and therefore the images to be unsuitable for surveillance use.  Placement of the outdoor cameras can possibly reduce the impact but in some instances, thermal cameras provide an alternative because the sensor does not respond to “visible light” of any kind.

    - Colour v Black & White Images

To an ever-increasing extent, surveillance cameras of all kinds are being offered with colour imaging.  Such images are very attractive and make recognition much more convenient.  There are challenges for colour imaging under low light conditions and some colour cameras change automatically to black and white images when the light conditions are reduced.  If artificial lighting is used it must have frequency spectrum and colour temperature representative of sunlight to ensure that the images are comparable with day lighting.  Sodium (HPS) or mercury (HID) lights, which have long been used in outdoor applications, make colour recognition essentially impossible.

    - PTZ v fixed lens v multi unit cameras v 360° cameras

PTZ (Pan, Tilt and Zoom) cameras are attractive to some designers but are an anathema to other designers.  Such cameras can cover a very large field of view using pre-programmed “tours” in which they move automatically through a pre-configured inspection of the landscape being surveyed.  As the image is being recorded it is clear that only the current image is recorded and depending on the frequency and nature of the tour, coverage of the landscape will be far from continuous.  In other situations, PTZ cameras are used by staff who may have reason to steer the camera image to look carefully to an aspect of an image observed on a fixed camera, e.g., a fixed camera image shows an apparent moving shadow along a security fence line which can be observed in greater detail by directing the PTZ camera to the same place at a much longer focal length (telephoto).  Some address situations of this kind by using multiple, single lens, fixed cameras instead of a PTZ cameras and manufacturers are now manufacturing single camera housings which include multiple imaging devices which can be configured independently or as a single defined group.  There is one other group of cameras which also have a very special feature in that they can provide a single 360° image.  Such cameras often include recording playback software allowing, for example, tracking of a person walking through an art gallery.  It is clear that selecting the correct camera configuration for any job is crucial.

    - Analogue v Digital Cameras

The cameras which are currently being used are digital, meaning that they include a direct connection on to the available LAN and no transformation of the video data is required.  Analogue Cameras are also defined by their encoding systems, such as NTSC and PAL.  The older, now largely outdated, cameras use analog signals which need to be converted to a digit signal to be transmitted over the LAN which is generally used as the means of interconnecting buildings and equipment.

- The design should be evaluated by using a camera simulation package to ensure that the resulting images meet all of the design intent before the construction is completed.

- These pre-approved surveillance devices are listed in the Appendix P “Digital Video Management System”.

- The Digital Video Management System (“DVMS”) is now, and shall continue to be, capable of supporting a further future expansion of the reconfigured system by a further 20% of cameras following completion of the current project.

- As a minimum, the system must support the most recent, currently available network cameras, encoders and camera streamers as may be available and are being used during the project execution.

- The Contractor shall use the latest generation of the equipment listed in Appendix P.  The contractor must ensure that all equipment which is being supplied will be compatible with the existing and previously installed components.  If any modifications or upgrades are required, these changes must be included in the project budget and identified in the proposal.

- It is the responsibility of the contractor to ensure that any upgrades or modifications of any kind to the existing equipment which is being proposed to accommodate the current project will in no way degrade or modify the performance of the existing installation.

- Hence the general industry guideline of using the most recent versions of software, firmware and hardware may lead to unsatisfactory performance due to incompatibility.  It should be noted that the existing installation may not have been updated to the latest versions because of prior, known incompatibilities.  The contractor is responsible to validate all such equipment and ensure full compatibility between newly supplied equipment and the already installed components.  Any proposed firmware or software updates must therefore be reviewed with the Region before any updates are undertaken.

- The DVMS shall, as a minimum, support the industry-standard Motion JPEG (MJPEG), MPEG-4, H.264, and H.265 as well as Axis’s proprietary Zipstream video compression technology formats.

- The DVMS system shall continue to be fully integrated with the Access Control system version currently in use by York Region and shall also be fully compatible with all announced updates to that system at the time of installation.  This system is being used as the primary user interface to monitor all surveillance cameras.

- York Region uses fixed lens cameras for surveillance unless otherwise stated.  All design decisions shall be made in consultation with York Region Capital Projects.

  - Video Recording Requirements

- The recording system must provide faithful and reliable recordings of all the cameras which are connected to it.  The recording system must use some form of RAID technology or equivalent technology so as to ensure that in the event of any drive failure the data will continue to be available.  Redundancy and fail over options must be included in the network to ensure that recording cameras is never at risk.

- Recording of a camera image is generally performed if there is motion in the field of view, although in some cases, recording can be performed continuously at a very slow rate until there is motion at which time the frame rate accelerates.  The recording is intended to analyse events after they have occurred and therefore it is important that the time prior to an incident can be recorded.  Such recording from before the event is often configurable to allow for the 2 minutes or for the 15 seconds before the “alarm went off”.  This is generally achieved by continuously recording to volatile memory.  Typically, recording is at a fixed rate, e.g., 15 fps and continuously erasing the data which is older than the configured time “before the incident”.  While cameras are continuously increasing their resolution, the current trend is to generally record at “1080” resolution for most surveillance applications.  The higher the resolution, the quicker the disks will fill when recording.

- It is by no means unusual to upgrade street or other lighting when surveillance is implemented.  Cameras are using more and more sensitive detectors but for high contrast and high quality images there may be a strong justification to provide lighting to eliminate shadows.

- Care must be taken when allowing for the amount of power which is required and the distance to the power source is mostly provided by POE data switches.

- While the recording of up to 300 cameras per NVR is normal, there can of course be unlimited numbers of NVRs.  The NVRs must have an accurate source of time so that images can be synchronised across the network.  Typically, the recorded image from each camera includes a burn-in, i.e., an image which is configured to show the date and time and the camera description on every frame of the recording.

- The recordings should be “searchable”, i.e., the NVR has an interface which allows for searching for specific images using a number of different criteria, such as:

    - Date and time

    - Alarms

    - Facial recognition

    - Location

    - Analytics, such as when a car drove into the driveway etc.

- While reviewing recordings to perform an investigation, security staff may review many images from many cameras and there needs to be mechanism to quickly return to the most useful images.  A good NVR will provide a “bookmarking” tool to effectively allow for the storage of particular scenes.

- Archiving of the recorded images should be performed automatically from the live NVRs several times (e.g., 4 times) during the day in order to offload the recorders to ensure optimal hardware performance.  The archived data can remain on the network where it is readily accessible for a limited period.

- The use of surveillance cameras and the retention of the recordings should be reviewed for compliance with the requirements of the FIPPA and MFIPPA which may have limitations on these activities.

- While it is commonplace to erase recordings which have “no significance” after a period such as 30 days, there are also situation such as a pending investigation which may take months to unfold.  The recordings associated with that investigation may need to be kept, protected and not available for review by any “unauthorised” person.  Such evidence will be secured with an “evidence lock”.

- If a recording is required by a law enforcement authority in order to prosecute a case, there may be a requirement to apply a digital signature so that, it can be shown in court, that the recording has not been modified or “contaminated”.

- There should be tools allowing for the security staff at the main control centre to forward the image of an incident which has occurred to “mobile colleagues” via their cell phones or tablets.  A similar operation must be available to send video images as files in e-mail messages.

- The NVR and its related components should not use proprietary hardware but adhere to industry standard configurations so that all computers used by the Region, can be maintained and procured from a single source.

- It is almost universal to incorporate an LPR program in the surveillance management software, with the ability to recognise any licence plate from Canada or the USA.  This function should provide for searching the recordings or monitoring for the appearance of a particular vehicle.  Note that the inconsistent requirement of one or two licence plates on a car can make such applications relatively challenging.

- The video system manufacturer should be able to supply an API or and an SDK.  These tools will allow developers to create tools to facilitate the use of the video recordings, e.g., transfer a video clip to a specific security guard or to notify a security officer each time when a particular entrance is used.

- The foregoing list is intended to identify the manner in which a modern video surveillance recorder can be configured and implemented.  The options are not exhaustive and have omitted the questions of reliability and ease of use which is taken for granted.

  - Elevator Access Control Integration

- There are a number of options which come into play when the decision to install elevator access control is made.  This section will identify the most common topics and issues.  Among such issues is the requirement that the designers understand some of the serious limitations which are discussed below.

- Basic elevator control is commonly achieved by installing a card reader in each elevator car.  When a user swipes their access card at the card reader, the floors that they have access to are unlocked for a short period of time, e.g., 7 seconds.  During this time, the user is able to select a floor by pressing the “floor button” inside the cab.

- The interface between the access control system and the elevator can be achieved in two very different ways.  Both require the card reader installed in the elevator car (cab) to communicate with the access control system electronics (typically a controller) which is generally located in the elevator machine room close to where the elevator controller is also installed.

- Access to the elevator control room is heavily regulated by the Elevator Code, the Elevator technician Union and the TSSA because of the inherent dangers of that location and it is common practice that an elevator technician may have to be present just to ensure safety and compliance.

- The approval of the floor control may require that the TSSA be involved.  The installation of the card readers in the elevator cab may involve the elevator technician’s presence because the work and the wiring are interpreted as “elevator work” although, again, this work is often performed by the security technician under the watchful eye of the elevator technician.

- In an emergency, such as power failure or a building fire alarm activation the elevator may need some special functions.  In the event of a power failure, it is commonplace for a standby emergency generator to power each car in a bank of elevators in turn so as to return all cars and their passengers to a particular floor, generally the ground floor.  In the event of a fire alarm the process is similar except that as long as there is regular power available, the cars will return to an exit floor expeditiously so as to provide subsequent availability for fire fighters.  It is recommended that in such circumstances the access control be automatically disabled to allow the first responders free access to all areas of the building.

- The vagaries of the Elevator Code require that the main exit floor is not normally a controlled floor, meaning that anybody in the building can freely use the elevator to reach the Ground floor from where there is an exit to the street.

- The concept of placing a card reader in the elevator cars and then locking some or all o the floors is not very “reliable” for a number of reasons.  The general situation in an elevator is that there may be a dozen or maybe more, passengers in the car as it heads upwards from the ground floor.  Often the passengers do not know each other and some will recognise that they do not need to press a particular floor because it has already been activated as shown by the illumination of that floor button.  Hence, an intruder just has to keep discretely quiet and then be taken to the “locked” floor to which he wishes access.  When this person wishes to leave, the departure generally requires no access card.  Note further that, when an authorised user is granted access during a brief time window to multiple floors, either the authorised user or a miscreant can press multiple buttons, thus directing the elevator to stop at multiple “locked” floors.

- The functionality which is described here can be implemented by interrupting all of the floor buttons which are to be controlled for each of the cars with a normally open relay contact.  The use of the card will cause the relays to change status for the permitted floors and to thereby allow the selection signal to pass through the contacts while they are briefly closed.  Once the timed process is complete the relays return to their open state which inhibits selection of any controlled floor from that elevator.  In almost all cases, all the elevators in a bank of elevators will be programmed identically.

- When the audit trail log is reviewed with regard to the elevator activity, there are 2 possibilities in regard to the amount of data which can be found.

    - Most commonly there is no “destination reporting” which means that the initial card swipe will unlock all the floors allowed by the access level accorded to that user, for example, floors 3, 4, 5, 6 and 7.  The user will swipe this card and the audit trail log will report that user “John Doe was granted access to floors 3, 4, 5, 6 and 7 in Car 5”.  When the user selects a floor there is no data capture of this information and therefore the audit trail log has no means of knowing to which floor this user was travelling.

    - A further complication which arises is that the other passengers on the elevator can press any of the other “unlocked” floors during the “unlock time”.  It is obvious that the unlock time has to be short, but it is equally clear that if it is too short, there will be complaints and if it is too long the security is weakened.  The recommendation is about 5 to 7 seconds as a practical compromise.

    - Many elevators have dual sets of floor buttons to simplify life for the passengers when the elevator is relatively crowded or to increase overall elevator reliability.  Since the panels work together, the single card swipe will unlock both floor button panels, thereby allowing selection of floors simultaneously from both sets of floor buttons.

    - With more sophisticated configurations it is possible to ensure that the destination floor which is selected is written to the audit trail log.  This then requires inputs to the elevator controller from the access control system.  The use of the relays as described above is combined with the detection of the current flowing in the one floor button circuit which is interpreted as the floor to which the elevator is being dispatched.  Clearly more wiring is required for this option and also more equipment.  Hence this option is more expensive and less frequently used.  In some situations, the functionality is achieved by using an elevator lobby which includes access control on all the entrances/exits from the lobby.

- Low level elevator integration with the access control system, as described above, enables cost effective access control of almost any elevator system, regardless of age or capability.  Basic integration is achieved by wiring the access control controller outputs directly to elevator floor relays, thereby allowing the access control system to control the “locking and unlocking” of floors.

- As an alternative, where required, elevator floor buttons can be connected to the access control controller inputs, enabling the controller to record which floor a user has selected when they are given access to the authorised call buttons in the elevator.  The access control system monitors the inputs from the car buttons and activates the selected floor relay to mimic the function of the floor button in the elevator.  By performing this function, the access control is responding to the floor call button and can record which floor that individual has selected.  Note that this does not prevent the person alighting from the elevator on any floor where the elevator stops.  The security system does not have any record of the floor to which the elevator is called.  This process is usually referred to as Destination Reporting.

- Some access control systems can also achieve high level interface (HLI) integration with selected manufacturer’s elevator systems.  In such installations the access control controller communicates with an elevator server or controller over the TCP/IP network (or other communications protocol such as BACnet) rather than using individual physical outputs and inputs.  Because each elevator system is proprietary, it is not really possible to provide more details in a generic format.  As is evident, many of the previously noted considerations still apply and the only major difference is that the integration between the elevator control system and the access control system is significantly less complex.

- Generally, when implementing an access control system for a new elevator installation, the card reader will communicate over a special cable incorporated in the “travelling cable” which travels with the cab and provides many conductors for the power, signalling, card reader, surveillance camera, ventilation and screen in the cab.  While this sounds straightforward, this process may not be trivial in high rise buildings where the cable length can grow rapidly.  For an approximate example, a building of 50 stories will typically have the travelling cable terminated at the 25th floor.  The cable itself has to reach up and down 25 floors and the link to the elevator control room from the termination is another 25 floors, i.e., the overall length of the cable will be about 60 floors of approximately 4.5 m each for a total of 270 m (890 ft).  As is obvious this length is significant and for much of the distance the communications cable is bound integrally with cables which may be carrying “dirty” electrical power.

- When installing a “retrofit” elevator access control system the recommendation is often to replace the travelling cable which is extremely costly and time consuming.  There are signal conditioning and signal amplification devices which are recommended as an alternative (see Appendix R -- Cabling, Conductors and Miscellaneous Accessories).  Since the elevator industry has long had the practice to equip the travelling cables with a generous number of spare conductors, there is generally no difficulty in negotiating for permission to use the spare power conductors in the travelling cable.  These conductors can be used in conjunction with the signal conditioner to connect the card reader placed in the elevator to the access control controller in the elevator room (which is where the travelling cable is terminated.  This link will then provide reliable card data from the elevator cab to the access control controller.

- The elevator technicians can provide suitable terminals in the elevator machine room for each elevator car where the security technician can connect the access control output relays to complete the control circuit.

- Control relays can be wired in either a normally open connection (fail secure) or a normally closed connection (fail safe).  The particular selection should be reviewed with the Region in order to determine which of these is more appropriate for any given project.  Depending on the cause of a power failure, the elevators may not be moving in the event of a power failure.

    - Fail Safe: When power is interrupted (fails), the electronic locking device is released (unlocked).  This is recommended for most “regular” applications and is mandatory if the installation is to comply with UL specifications.

    - Fail Secure: When power is interrupted (fails), the electronic locking device is secured (locked).  This option may be preferred in an environment where individuals are at risk if they have freedom, e.g., protective custody.

- The floor call buttons for the access control function must be interrupted on all the elevator cars independently and programming is then configured to allow the same functionalities on all the cars in the group.  The card swipe identifies the car which is being used and only the call buttons in that elevator will be activated.

- Although breaking either side of the call button wiring will provide the same functionality, it is recommended that the elevator company, break the “control signal” and not the “common supply” for the button.  This method allows a simple migration to destination reporting if required in the future.

- Because the elevator “service mode” generally does not use the floor call buttons, the access control does not generally affect the service mode.  Thus, when the elevator service technicians use a key to activate the “service mode” there is no inconvenience for them.  The janitorial staff often use the service mode so that they can keep control of the elevator which will not respond to any “regular passenger dispatch requirements”.

- The service mode will then not record who is using the elevator or where the elevator is travelling and there are no restrictions on the floors to which the elevator may be taken.  A modification can be incorporated whereby use of the key to activate or deactivate the service mode in each cab is associated with a unique “input” and the change of state is logged.  This change of state is best identified at the elevator controller.

- If the card reader loses contact with the controller, it causes a communication failure but not necessarily a system notification.  Suitable programming allows an option of choosing whether to automatically allow or prevent access to all controlled floors in this situation, i.e., to fail safe or fail secure.

- Optional programming of the access control cards can provide the ability to lock floors based on a suitable schedule.  Thus, for example, schedules can be defined so that guests who do not have suitable cards can access the floor with the office reception between 9:00 am and 5:00 pm, staff can access certain floors including the reception from 7:00 am to 7:00 pm and the security guards can have 24 hour access.  The freight elevator can of course have an independent set of schedules and access privileges.

- The elevator access control does not offer the concept of “door forced” or “held open” as managed by the security system.  All elevator operational alarms are routed to the elevator controllers and are unrelated to the security system.

- In some buildings there will be multiple tenants who do not use the same access cards or even use the same security system.  Such situations can generally be resolved successfully while using a single card reader providing there is cooperation between the tenants and the landlord.  The details are beyond the scope of this document.  In brief, the card reader (which may be multi-technology capable) output is sent simultaneously to each of the associated security systems i.e., the security system for each tenant, and providing that the card numbers (including the facility code) are unique no more than a single system should grant access to any given card.  Clearly precautions are required to electrically isolate the inputs and outputs but even this is readily achieved.

- In some cases, multiple tenants may have the security of their office space managed for them by the a single, landlord managed access control / intrusion detection system.  The foregoing description provides an alternative and offers some potential advantages:

    - No personal or personnel information is divulged to the landlord;

    - Multi branch operations can use a single card for all offices across its available networks;

    - Updating of cards etc are under the company control, meaning fewer delays to implementing changes; and

    - The tenant can determine their own security policies and equipment selections.

- It is strongly recommended that there shall be a simple toggle switch (or key switch) associated with the relay bank for each car which is controlled by the access control system.  This will avoid any disputes between the elevator contractor and the security system contractor and accelerate problem identification, if or when, there is any problem related to the elevator call buttons.  This switch will have 2 positions, namely “normal operation” where the access cards allow access to the locked floors and “bypass” where all the relays permit free access to all floors and the elevator operates as if there was no access control system.  In this way, the building staff can unequivocally identify if a problem lies with the security system or with the elevator controls.

- In most elevator access control applications, the fire alarm system has to have the ability to “recall” the elevators to the “main” floor where the fire department can readily access and use the elevators as they may require.  In the presence of an access control system the fire alarm system should also “bypass” the access control function to ensure that the fire department can travel freely through the building as may be required.  The extent of the “fire alarm induced bypass action” will need to be considered and this may be a Code related matter.  In particular the locking of floors in the elevator may be irrelevant when the elevator is being used in fire fighting mode (see service mode above) although using an addressable relay on the fire alarm system to “bypass the relay bank” as described above is a very simple procedure.

- The access levels with permission for the users’ access cards must include the floors to which the users require access.  This can be achieved either by creating new access levels for the floors or by adding the elevator floors to the existing access levels which already span different floors.

- The access control (security system) does not in any way alter the requirement for emergency voice communications for passengers in the elevator as required by the Elevator Code.  There is currently no requirement to place surveillance cameras in elevator cars but, increasingly, such cameras are being installed to ensure the safety of passengers.

  - Network and Video Cabling

- Network and Video Cabling devices are not defined specifically for a particular project and shall adhere to the industry standards and performance criteria as identified in Appendix D “Standards Applicable to Regional Security Projects” or, as may be otherwise defined by the Region and by the ITS department as in its Corporate ITS Cabling & Wiring Standard (February 8, 2021).  The information cited here is, in part, extracted from that document.

- The form of communications between the proprietary components of the security system is not mandated by this section but shall address the requirements of the security system.  The cabling for such communications will generally be based on similar standards to those advocated here.  Sharing of any pathways, labelling and termination considerations shall follow the same guidelines as for the Local or Wide Area Networks as described here.

- A Local Area Network (LAN) shall be provided for communication as may be required between the security system elements and the existing ITS infrastructure.  All interfaces which are attached to the LAN shall be configured, where possible, for a minimum of 1000BaseTX Ethernet (1Gbps).  It is noted that some security equipment functions with lower data rates and all high-speed equipment can operate at lower interface speeds.  The LAN may need to use additional technologies within the backbone for greater speed or distance.  Acceptable technologies are:

- FDDI (Fibre Distributed Data Interface)

- 1000BaseSX or 1000BaseLX Gigabit Ethernet (fibre)

- Asynchronous Transfer Mode (ATM)

- 1000BASE-TX UTP

- The LAN shall use industry standard network cables.  Acceptable cable types are:

- OM4 Optical Multi-Mode, 50 µ Core diameter / 125 µ cladding diameter, Class 1a, graded index optical waveguide Fibre.  All connectors shall be LC compliant and conform to ANSI/TIA-492AAAC.

- Category 6 (250 MHz) or better, Unshielded Twisted Pair (UTP) terminated using TIA 568A configuration.

- Each fibre backbone cable shall have a minimum of 12 strands OM4 distribution type fibre.  The OM4 distribution type fibre shall perform as per industry standards over the required distances defined for the site.

- Where there is a requirement for backbone interconnection between wiring closets on the same floor or multiple floors, such interconnection shall use a minimum of a 6 fibre strand, duplex, multi-mode 50 / 125 µ (OM4) rated fibre optic backbone terminated with:

    - 1 U x 19 ins rack mounted fibre patch panel

    - Connectors shall be OM4 (minimum), LC style;

    - ¾ inch fibre inner duct (corrugated) rated at FT-6 for ceiling plenum or FT-4 if the plenum is not used as a return air plenum;

    - Pulling force shall be limited to the maximum force permitted by the manufacturer;

    - Bend radius of the conduit and inner duct shall not be smaller than permitted by manufacturer’s specifications; and

    - The inner duct shall be restrained so that the fibre inside of it is protected and not unnecessarily stressed.

- Cable Distances in excess of 100 m (330 ft) shall use multi-mode fibre (as opposed to UTP).

- All connectors for the termination of fibre optic backbone cables shall use duplex LC connectors.

- Fibre optic enclosures shall meet the following requirements:

    - Enclosures shall include a slide out drawer for frontal access of the terminations.

    - Enclosures shall be compatible with LC connectors.

- For multi-mode fibre optic terminations inside access closets fibre patch panels the connectors shall be preloaded adapters configured with LC duplex, multimode, adapters.

- The LAN used for surveillance and security applications shall be logically and/or physically separate from any other existing LAN infrastructure.  Interconnection to other LANs shall only be through one of the following:

- A router;

- A Layer 3 capable network switch; or

- As an additional VLAN to the existing LAN equipment.

- Where the design requires an interconnection between VLANs, a router or a Layer 3 capable switch shall be provided by the Contractor and be approved by the ITS department.

- Network video cables shall not be connected individually to the Camera Server.  All communications with the Camera (DVMS) Server shall use the LAN.  Each network camera or video streamer shall have a single Ethernet network connection which is to be used both for video and also for camera control, e.g., for Pan/Tilt/Zoom (PTZ) communications.

- Cameras shall be powered using POE switches and, only in exceptional cases, will power injectors or local power sources be approved by the Region.

- Supply a complete and working Closed-Circuit Television System (CCTV) System and Digital Video Management System (DVMS).

- All camera passwords shall be changed from their factory defaults to a password provided by the Region.

  - Conduits, Pathways, Fittings, Cables and Miscellaneous Accessories

- The construction of all conduits and associated components shall comply with the requirements of the Ontario Electrical Safety Code (OESC) and with other requirements as stated in Appendix Q: “Conduits, Fittings and Accessories” and in the Contract Documents.  This compliance requirement applies even if the conduit is not being used for electrical applications.

- All new communications conduits are limited to a fill capacity of 30% of the cross-sectional area.  The industry practice and Codes allow for 40% fill but new conduits shall allow for a future expansion in cable occupancy to 40% fill.  Where existing conduits are being reused by addition of new cables the conduits may not exceed 40% fill upon completion of the construction.

- All cabling, wiring and conductors shall comply with the requirements set forth in Appendix R: “Cabling, Conductors and Miscellaneous Accessories” and, as applicable, are also subject to the specifications as defined in the OESC including the fire rating FT-4 or FT-6 and CSA or equivalent certification.

  - Parking Controls

- Details pertaining to the specific equipment for Parking Control may be found in Appendix S: “Parking Barriers”.

- The Parking Control Devices are activated through and also, largely report, all status information through the use of dry contacts.  Therefore, unlike many of the network connected security devices, the Region is largely agnostic to the choice of parking equipment supplied by the contractor.

- Because York Region does not have pre-approved equipment for Parking Barriers it will evaluate and approve submissions for specific products on an individual case basis.  Submissions for each project must include the Gate Manufacturer and proposed model, reference to existing operating installations and provide assurance of parts and maintenance availability.

- Barrier arms shall break away readily and shall be readily replaced.  As applicable, the barrier arms shall be illuminated to allow high visibility when available illumination is poor.

- All control functions for the operation of barriers are to be controlled through the Access Control security system.

- Where supply and installation of high-speed automatic rising barrier for vehicles is required for access control, the barrier arm is to open via authorisation given in response to valid card reads using a multi technology card reader compatible with the access control system.

- The pedestal on which the card reader and intercom are installed will generally be designed to facilitate use by trucks or passenger vehicles by providing suitable readers at 2 different heights.  Further details are provided in Appendix S, “Parking Barriers”.  There is to be a long-range card reader for use by truck drivers which is mounted so that the driver can hold the access card in line with, but distant from the long-range reader (up to 24 inches).  There will be a second, traditional reader, keypad and intercom installed at a suitable height for use by passenger vehicle drivers who are able to reach the reader, the keypad and the intercom directly from the “driver’s window”.  The actual geometry and distances may vary by project but must be approved by the Region.

- Alternatively, “visitors” wishing to enter the parking area may use the intercom to ask for remote release of the entrance barrier which will be provided through a manual operation from the Central Operations Centre by using the access control system.

- Suitably placed cameras should be associated with the audio intercom to capture the driver’s face and the vehicle identification.

- The access control system will provide a NO, momentary, dry contact closure to activate the entrance barrier arm, whether activated by the use of a card swipe or via the operator response to an Intercom request.

- There will be 2 vehicle detector loops in the entrance lane to streamline the barrier operation:

  - The first loop will ensure that the barrier arm will only open when there is a vehicle at the reader location, i.e., a pedestrian cannot open the barrier arm and then allow an “unauthorised” vehicle to have access.

  - The second loop will be triggered as any entering vehicle passes beyond the raised entrance barrier so that the barrier will then lower.

  - These loops will not function in reverse, i.e., the barrier will remain down if a vehicle attempts to exit via the entrance.

- The barrier arm is to open on vehicle exit by means of a vehicle departure sensing loop and a reset loop.  The departure loop senses the vehicle and opens the arm which recloses when the “reset” loop detects the departing vehicle.  These loops should be designed to prevent and detect illegal entry and are more fully described in the Appendix S.

- The barrier arms shall be designed only for passenger cars or small trucks, or for both passenger and commercial vehicles as may be required by the Contract Documents.

- Lighting shall be integrated into the barrier arms to ensure clear visibility during night time conditions.

- All barrier arms shall incorporate breakaway features.

- Provisions shall be incorporated to allow for the configuration of the barrier arms to permit anti-passback operation if required by the Contract documents.  This configuration would require the use of a card reader instead of a detection loop to activate the exit barrier arm.  The exit lane would therefore also have to be equipped with a pedestal allowing for dual height readers (as in the entrance lane) and an intercom to facilitate any calls for help.

- The gate shall also be able to open and close with a configurable timer or through a maintained contact from the access control system.  The timer will enable the barrier arm to be closed during certain hours, e.g., parking lot closed after 8:00 pm until 7:00 am or the barrier arm can be open continuously from 9:00 am until 5:00 pm.

- Security system installer to ensure that the barrier arm is integrated with security system, i.e., barrier arm status information is provided to the access control system where it shall be logged.

- Provisions shall be included to ensure that the entrance and exit barrier arms cannot close onto a vehicle which is either stationery under the barrier arm or moving through either the entrance or the exit lanes.  However, should the situation arise where the barrier arm encounters an “object” such as a car while it closing, the barrier arm shall immediately signal an alarm to the access control system and reverse direction and stop operation when it is completely open.  The barrier arm shall provide sufficient information so that all of its operations, i.e., open, close and close followed by “hit an obstacle and open” shall be logged by the access control system.  Time stamps from these logs shall be synchronised with the recorded surveillance images thereby allowing detailed information about the arrivals and departures from the parking areas.

- Provisions shall be included so that the barrier arm can be manually operated locally in the event of a power or communications failure.  Usually this is achieved by key operated, weatherproof switches on the pedestal.  Such manual operation will not respect the signals from the detection loops.

- The parking system as proposed shall include any required options necessary to ensure that the system shall operate reliably under any and all anticipated environmental conditions (see Appendix H: “Environmental Requirements”).

- All civil, electrical and communications requirements shall be identified in the proposed implementation and submissions.

- Provisions shall be included in the design to provide physical protection of the barrier arms, e.g., posts to protect against vehicular collision, warning lights to identify the barrier arms and kerbs to control vehicle location.

- As described above, the parking barriers shall use detector loops and loop amplifiers to control the entrance and exit activities which depend on vehicle presence detection.  Apart from the requirement that these loops be reliable for all types of vehicles, i.e., large, small, multi-axle, high bed or low slung, aluminum, steel or plastic bodies and that the amplifiers be readily integrated into the access control system, York Region will evaluate the suitability of any properly proposed submission.

- The vehicle detection loops shall be placed in the travelled lanes to provide the required functionalities and to assure the Region of reliable performance in the environmental conditions as described in Appendix H.  Note that the Region has no preference as to whether the loops are pre-formed or are formed in situ.  The loops shall however withstand the technologies used to keep the roadway clear of ice and snow as well as sun and rain.

  - Locksmithing and Door Hardware

- Details pertaining to the specific requirements applicable to keys and locks may be found in Appendix T “Locks”.

- All doors are to be equipped as outlined in the associated Security Device Summary document.  Where specific details regarding locks are not available, doors should be equipped in accordance with the requirements laid out in Appendix T: “Locks”.

- Interior exiting through any door (not overhead doors) should involve the use of a push paddle or panic crash bar exit device installed at a standard height not exceeding 1,200 mm (approximately 48 ins) AFF as required by the OBC.

- York Region does not have a registered keyway or a dedicated locksmith.

- During the construction phase, the Contractor shall supply temporary cylinders keyed to any convenient, secure combination.  The Region shall be given five copies of the keys providing access to the area under construction for emergency and security patrol use.

- There is no general policy regarding provision of grandmaster or sub master keying of locks and the Contractor shall comply with the requirements as defined in the Contract Documents.

- Upon completion of the construction, three passkeys shall be provided for each door on which a final lock cylinder has been installed and the combination of each shall be recorded by the Contract Administrator.

- The final lock cylinders or cylinder core shall be installed only after the final commissioning has been successfully completed.

- Details of the locksmith providing the cylinders and keys as described in this section shall be furnished to the Region as part of the required As-Built Documentation.

- Door hardware which is not defined in Appendix T: “Locks” shall meet all required standards and specifications as provided in the architectural specification and is therefore not specified in this security document.

  - Universal Washroom Requirements

- A universal washroom is an enclosed space with a barrier free toilet, sink and turning space so that a wheeled mobility device may be accommodated.  These washrooms aim to provide privacy and dignity for people with a disability, including for those who require an assistant.

- The details of the washroom requirements are generally specified in the Ontario Building Code, particularly in Section “3.8.3.12. Universal Washrooms” but only those portions related to control of the door and those functions related to the “emergency button” are being addressed in this document.  All other aspects of the washroom construction fall under the General Contractor and the Architect’s mandates.

- OBC 3.8.3.12.2 states that:

A universal washroom shall have,

  - an emergency call system that consists of audible and visual signal devices inside and outside of the washroom that are activated by a control device inside the washroom, and

  - an emergency sign that contains the words “IN THE EVENT OF AN EMERGENCY PUSH EMERGENCY BUTTON AND AUDIBLE AND VISUAL SIGNAL WILL ACTIVATE” in letters at least 25 mm high with a 5 mm stroke and that is posted above the emergency button.

Additionally, the OBC states the following requirement:

Ensure emergency alarms are linked to a centrally monitored switchboard for facilities that have the capability.  If third party monitoring is not available, alarms will remain local.

- The security Contractor is to ensure that the emergency button alarms are reporting to the access control system.  Monitoring of the washroom alarm will be implemented both locally, i.e., by the Region, and also by an off-site, 3rd party monitoring station.

- All devices identified in Appendix U: “Universal Washroom” are to be purchased and installed under the General Contractor’s Contract or through any designated subcontractors.

- Note that there are Code compliant kits available from some key manufacturers which provide all the required devices to provide the control functions for the washroom door.  Such kits are outside the scope of this security document.

- Details of the approved hardware to implement the control and monitoring of the Universal Washroom can be found in Appendix U: “Universal Washroom”.

- EXECUTION

  - Electrical Installation

- The Electrical work required under this contract shall conform to the requirements of the OESC and meet with the approval of the ESA.

- Electricians working on the site shall adhere to the requisite safety procedures and Best Practices required to protect themselves from any risks arising from potential Arc Flash sources.

- Electricians shall not work on “hot circuits” without special permission from the Region.

  - Installation – Wires and Cables

- Provide wires of number and gauge (including corresponding raceways) as required, with sufficient space for conductors as indicated in the Drawings.  Provide adequate wiring for the actual equipment which is being installed.  There is no requirement to make allowance for future expansion by using oversized conductors or excess numbers of conductors.  As noted, conduits shall have spare capacity.

- Provide wire and cable according to the drawings and security system requirements.  This includes consideration of wire types (related to environmental criteria) colours, conductor types, jacketing, conductor type and gauge.

- Pull cable into ducts, conduits and cable trays in accordance with cable manufacturer’s recommendations.  Use specialised cable grips suitable for cable type, or pulling eyes fastened directly onto cable conductors.

- Limit pulling tension and minimum bending radii to those recommended by manufacturer.  Also observe that the conduits which are being used must adhere to the Code limitations regarding numbers of bends, lengths of pulls and provision of pull boxes.

- Prevent damage to cable jackets by utilizing adequate amount of approved lubricant when pulling cables through ducts and conduits.

- Support cables in manholes and utility tunnels on cable trays or cable racks.

- Arrange cables in parallel rows on cable trays.  Maintain cable spacing by fastening cables, with Velcro, a minimum of every 2000 mm on straight horizontal runs and to each rung at bends, including two rungs of adjoining straight sections.  Fasten cables on vertical tray runs every 1000 mm.  Limit the number of cables in each bundle of cables in accordance with best practices.

- Connect cables to electrical boxes and equipment enclosures located in outdoor, wet or sprinklered areas with watertight cable connectors.

- Provide cable grips for vertical and horizontal (catenary) cable suspension installations to reduce cable tension at connectors and at cable bends.  Provide supporting messenger cables in accordance with best practices.

- Install through wiring in junction boxes and pull boxes having no connection within the box.  Leave a minimum of 300 mm (12 ins) of slack inside box or follow best practices in accordance with the type of cable and the location.

- Facilitate making of splices and connections by leaving sufficient slack length of each conductor at panel boards, outlet boxes and other devices.  Typically, the conductors should allow for 3 m (10 ft) of spare cable during the cable pulling process prior to the termination and dressing of each cable.

- Where suitable, e.g., outdoor or below ground, seal the conduits after completing the cable installation to mitigate the risk of rodent damage to the cable jackets.  The sealant being used shall be designated for this purpose and shall be approved by the Region.

- Install instrumentation/system (low voltage) conductive signal wires in separate raceways from power and control wiring as is required by Code.

- Identify each cable by attaching a cable marker at each end, in all intermediate manholes, junction boxes and pull boxes.  (See Appendix V: “Labelling Requirements”.

- Install cables so as to conserve headroom in exposed locations and to minimize the amount of interference in spaces through which they pass.

- Where exposed, install raceways, conduits and cables parallel or perpendicular to building lines and group neatly.

- Maintain the integrity of all fire separations by sealing around all cables, trays or conduits where they pass through such fire separations.  Generally, this includes all floors, ceilings and concrete or masonry walls.  Fire stopping may be performed with approved materials meeting the NFPA requirements or by means of manufactured systems which may more readily permit later additions.  In all cases the resulting installation must meet or exceed that of the existing barrier.

- As far as is practicable, all feeder wiring shall be continuous from origin to panel termination without installing splices in intermediate pull boxes or splicing chambers.  Sufficient slack (typically 3 m or 10 ft) shall be left at the termination point to make proper connections to the equipment.  Any splices must be in accordance with the requirements of the Code and best practices.  The communication cables may have specific length restrictions and splices or intermediate connections are generally not permitted.  All splices or junctions must be readily accessible, i.e., must be visible and accessible subsequent to completion of the project.

  - Installation – All Security System Devices

- Supply, install, configure, test, and commission all the access control system and intrusion detection system components, communications equipment and all system components to ensure the functionality of complete security system and network.  All of the pre-approved equipment which is used to create these systems are listed in Appendices J, K, L, M, N and O.  The contractor shall identify and report all pre-existing or related construction defects which will affect the progress of the Work to the Region and the Consultant before commencing construction.

- The Drawings included with the project Specifications have been developed on a conceptual basis.  The Contractor is responsible for providing/verifying the quantities and part numbers contained in these documents which are based on the pre-approved products as listed in the above-mentioned Appendices.  The Contractor shall also itemise all additional components, cables, etc. which are required to complete the Work as defined in the Specifications and on the Drawings.  The Contractor shall also itemise the Bill of Materials in a logical, per building, per floor, and per area manner.  The detailed design shall be done by the Contractor who shall verify the part numbers and quantities which are required.  The contractor shall include any recommended spare parts as may be appropriate.  In particular, the contractor shall also identify any compatibility issues, should these exist, between the existing installation and the proposed new equipment.

- Please refer to the drawings provided with the Contract Documents which identify the project requirements, the security device summary document, the Specifications and the Appendices for the specific security, locksmithing requirements and any other needs related to this project.

- A minimum quantity of 20% of inputs and 20% of relay outputs are to remain available for use in all systems which are being affected by the project unless otherwise stated.  Unless otherwise noted in the Contract Drawings and Documents, the total quantity of inputs and outputs in the security system shall be less than 80% full, leaving a minimum of 20% capacity available for future use.

- All of the security system hardware and devices and additional nodes, as may be identified during the detailed design, are to be housed in NEMA 2 (IP11), NEMA 3 (IP54), or NEMA 4 (IP66) rated enclosures as listed in Appendix J or approved equivalent to suit the application.  All enclosures are to be wall mounted and located as shown on the drawings.  The Region will review and, as appropriate, approve the recommendations proposed by the Contractor.

- The enclosure sizes shall be sufficient to ensure ease of maintenance, adequate ventilation, and space for the elsewhere defined potential for 20% expansion.

- Where cabinets are exposed to the environment (see Appendix H “Environmental Requirements”), the Contractor is responsible for ensuring that the cabinet incorporates sufficient ventilation to ensure that the temperature inside the cabinet remains within acceptable tolerances, even when considering direct sunlight or winter storms.  Such ventilation may require heaters, fans or air conditioning along with suitable thermostats.  While some equipment to be housed in such cabinets may, for example, be rated for operation to -20°C, the condensation which occurs at temperatures below 5°C is of itself damaging and is therefore to be avoided.  The Contractor shall provide suitable calculations and design information to justify the solution which is being proposed for such cabinets.

- Equipment location and other mounting locations may be modified with prior approval from the Region.

- The pre-approved Power Supplies are listed in Appendix J: “List of Approved Security Equipment” and shall be installed with a back plate.  Only the approved power distribution modules are to be used for the system design.

- Enclosure and Power Supply solutions are to be presented to the Region for approval.

- All control panels, where applicable, are to be equipped with local battery backup power.  Control panel batteries are to consist of 12V, 7Ah sealed lead acid batteries.  Batteries shall be labelled with the installation contractor name and the date when initially installed and this information is to be updated when the batteries are replaced (see Section 1.4.22).

- All equipment is to be installed according to the manufacturer’s recommendations and the Region shall be informed whenever such recommendations are not being followed.  The Region shall receive an explanation or justification when such conditions occur and direct the Contractor accordingly.  If any instances are identified by the Region where the manufacturer’s recommendations have been disregarded, corrective measures may be required by the Region.  Any such modifications shall be at the Contractor’s costs.

- All security system control panel enclosures must include:

  - Tamper switches on the cabinet door(s);

  - UPS back up (as may be required by the Region);

  - Key operated lock on the cabinet door(s);

  - Battery backup;

  - Switched LED light inside panel to facilitate maintenance (as may be required);

  - Clear and approved label on the outside;

  - Internally stored configuration documentation etc;

  - A dedicated network jack for maintenance purposes; and

  - A dedicated 120VAC power circuit.

- The Contractor shall supply all necessary wiring, termination equipment/devices and other necessary miscellaneous components which are not specified in the Contract Documents but which are necessary to implement a fully functional access control, intrusion detection and security system as well as mechanical/electromechanical key locking system.  Details for lock placement, function and keying can be found in the associated Security Device Summary document.  The door lock override key shall be the Medeco Intelligent Key Systems – M3 & X4 CLIQ (see also Appendix T: “Locks”).

- All cables and wires shall be CSA or equivalent approved and have a flame test rating equal to, or greater than, that required by the local building or fire code where it is being used, including the OBC and OESC and be clearly marked with the seal of approval by the testing agency.

- End of Line (EOL) supervision shall be used on all sensor connections monitoring door status or other conditions.  End of line resistor packs shall always be installed at the remote end of the detection line and not at the control panel.  The Contractor shall install resistor packs using either one resistor (2 state monitoring) or using two resistors to provide 4 state monitoring.  Resistance values are determined by the manufacturer of the equipment which is being used and the Region will define where and how such supervision implementation is to be installed.  Both of these “supervision” configurations will alert the intrusion detection system when the connection wires are cut or short circuited and signal a “tamper trouble” status.

- All cable runs should, where possible, be installed using a continuous, splice free cable run.

- If splices are required, the splices shall be made in CSA or other approved junction boxes utilizing DIN rail-mounted terminal blocks.  Splice box locations shall be marked on the wiring diagram and included in as-built documentation.  All splice locations shall be clearly marked in accordance with the requirements identified in Appendix V “Labelling Requirements” and shown on the drawings.

- Wiring lists shall be permanently affixed inside all cabinets where splices, or control components are installed.

- Security wiring should not be run in parallel within 30 cms (12”) of 110 VAC or higher voltage electrical wiring or conduit.

- All wiring shall adhere to applicable local, Provincial and Federal Codes and industry Best Practices shall be followed (also see Appendix D: “Standards Applicable to Regional Security Projects” for a partial list).

- The location of equipment shown on the Drawings may be revised during construction prior to its installation and the Contractor shall not be entitled to any additional costs for the relocation of equipment if the new location is within 10 metres (33 ft) of the original location.

- The contractor shall provide unit costing for each item in the Contract Documents which shall apply for all quantity changes of increase or decrease within +/- 5% of the quantities specified in the original documents.  If the change exceeds this limit, then the job shall be repriced.

- Install transformers complete with mounting brackets and hardware in positions in accordance with the manufacturer’s instructions and where approved by the Region.

- The Contractor shall provide all necessary lugs and mounting equipment which are not already provided with transformers and which are not individually specified.

- For the Regional Water and Wastewater facilities, the Control Panel relay outputs are to be wired to a local facility field controller so as to provide security system discrete dry contact inputs to the SCADA system.  Inputs which are to be wired in a fail-safe mode include:

  - Intrusion Alarm

  - Security System Armed

  - Security System Disarmed

  - Spare

- Communications between all of the distributed security devices and the York Regional Security servers shall use TCP/IP.  The internal communication between the security devices and the prime security system interface port will use a protocol determined by the equipment manufacturer and, as long as it is does not involve the Region’s networks, does not need to be documented or approved by ITS.  Configuration and activation of switch/hub ports on networking equipment maintained by the Region’s Information Technology Services Group (“ITS”) is to be co-ordinated by the Region.  The Contractor shall provide one (1) week advance notification to the Region’s ITS Group for configuration of network ports.

- IP addresses shall be provided by the Region’s ITS department on request.

- If local IT Network infrastructure linking from the remote site to the Regional security servers is not present, Wireless network equipment shall be used.  York Region ITS will supply the pre-configured Wireless Modem and network switch as well as the installation guidelines, (see Section 1.8 “Network TCP/IP Coordination”).

- The Network switch which is being used to communicate between a remote location and the security server shall be housed within the security system enclosure at the remote location.  Both the modem and the switch should be powered from UPS power supplies.

- All replaced or surplus equipment is to be delivered to the Region upon completion of this Contract for possible re-use.

- Where magnetic locking devices are to be used, and where permitted by Federal, Provincial, Local Municipal or Town/City Codes, all necessary permits, engineered drawings and fire alarm interconnection shall be completed by the Contractor.  Modification of the fire alarm system, signage and security systems, as may be required, shall be performed by the Fire Alarm System contractor of record for that location and by the Contractor as appropriate.

- Pre-Approved magnetic locks are shown in the Appendix T, “Locks”.  Such locks shall be Plate Magnet style locks with a minimum of 1200 lbf (540 kgs) holding force.  In addition, they shall have indicator LED’s showing if they are closed or open and have integral Hold Force Sensors (HFS) (Bond Sensors) and Door Contacts.

- Where electro-magnets are being installed for a double door entrance, the magnetic lock shall be equipped with 2 electromagnets and 2 “plates” enclosed in a single housing.  Door status monitoring may interpret the 2 doors as a single “opening”.

- The installation of the electromagnet may depend on the direction of “emergency egress” and wherever possible must be on the secure side of the door opening to reduce the risk of malicious attacks.

- The final inspection regarding permit approval of the magnetic lock inspection shall be coordinated by the Contractor and shall take place in the presence of the Region’s Project Coordinator.  Presence of other required participants shall be coordinated by the Contractor.

- All manufacturers’ requirements and electrical Code requirements for grounding and bonding, including the requirements of the OESC and OBC, shall be followed.  For larger projects there shall be 2 independent grounds, the power system ground and the telecommunications ground.  Ground wires, ground lugs, grounding bolts and ground bars shall all be made of copper or bronze.

- Concealed magnetic door contacts are to be installed on all exterior access doors and interior doors, as identified on the Device Summary Chart as well as on the Contract drawing.

- Electric door strikes are to be installed on all doors which are identified within the Device Summary Chart as well as the Contract drawings.  The electric strike shall be fire rated where these doors are a part of a fire separation.  The strikes shall be configured to fail secure, i.e., when there is no applied power, the door shall be locked.  Door key cylinders and locks shall be installed in every such door to allow key override of door strikes in all doors equipped with electric strikes.  A message will be generated by the security system noting that the door has been “forced” when the door is opened using an “override” key.

- The Contractor shall install snubbing diodes in all security devices incorporating electro-magnetic devices to minimize the induced reverse voltage which occurs when such devices are deactivated.  Such diodes shall, for example, be installed close to all electric strikes and electro magnetic locks to maximise protection.

- Installation of all electric strikes shall incorporate use of an “in-line power controller” to reduce the voltage supplied to the electric strike after the initial voltage surge activates the device.  This device must be rated for the electric strike which is being installed and is intended to protect strikes which remain powered for long durations, such as an office entrance which may be opened by a schedule at 9:00 am and then powered until the office closes at end of the day.  This is to be installed on all strikes to facilitate future applications of any door.  The Contractor shall certify the use of such “in-line power controllers” so that the Region may exploit the doubling of the factory warranty period on such installations.

- The Contractor shall label all enclosures containing security equipment identifying the nature of the equipment and the addresses of the enclosed nodes.  All networked equipment is to be labelled with the corresponding IP information.  Main alarm outputs and relays shall be labelled accordingly.  All alarm points, card readers and other system components shall be labelled in accordance with the door numbering and description syntax.  All labelling shall be consistent on site, in the as-built documentation and in the software.  Labels shall be weather/environment resistant type (see Appendix V: “Labelling Requirements”).

- The contractor shall post warranty/contact information on the inside of the main control enclosure for each facility.  Where possible this information should identify contact information which is operational 24/7.

- Dedicated security system alarm outputs shall be provided for all Environmental Services facilities and connected to the SCADA control panel so as to provide integrated monitoring of intrusion detection alarm and arming status (see Section 3.2.26).  The SCADA system accepts only dry form C relay contacts, i.e., NO and NC contacts.  Integration with the Region’s SCADA system must be coordinated with the Region, 2 weeks in advance of the integration so as to have a representative from Environmental Services scheduled to be present and assist with the integration.  All work undertaken in chemical rooms (chlorine, ammonia rooms) at Environmental Water and Wastewater facilities must also be coordinated with the Region in advance to have a representative from Environmental Services scheduled to be present.

- The Contractor is responsible for programming and testing of the intrusion reporting component if it is to be monitored by a 3rd party Central Station.  The Contractor is to coordinate with the central monitoring station for configuration and testing of the system for all relevant signals.  The intrusion reporting system at the Region’s sites shall be equipped with both Wireless and IP-Wired communication modules.  The Contractor shall supply, install, configure, test and commission a compatible cellular communication module(s) complete with an active SIM card and an application appropriate antenna, i.e., the contractor shall enroll the security system as a subscriber.  This antenna is to be installed on the inside or outside of the building so as to ensure a consistent and reliable signal and shall be in accordance with the requirements of applicable laws, including municipal, Provincial and Federal legislation and regulations.  The contractor shall coordinate the subscription with the Region and establish the appropriate response plan for each of the alarm points.  If there is an existing contract with a local monitoring service, the Contractor shall modify the existing contract to allow for the added service.

- The Contractor shall ensure that the cellular service and the monitoring service are so configured that the billing and other communications from the carrier are routed as requested by the Region.

- All Alarms shall be the only notifications communicated to the 3rd Party Monitoring Service.  No pre-alarms (as are associated with the Door Held Open alarms) shall be communicated to the 3rd Party Monitoring service.

- The Contractor shall configure a routine test alarm transmission to the 3rd Party Monitoring Service which shall be set up to independently confirm the operation of both the wireless and the IP communications links during the silent night hours e.g., 2:00 am and 2:15 am every 24 hours unless otherwise instructed.

- The Contractor shall work with the Region to confirm the:

  - Unique and unambiguous naming of all the alarm points;

  - Name and contact information of three contacts for each alarm point; and

  - A suitable Response plan for each alarm point.

- The Contractor shall ensure that the response plan and contact information is confirmed with the 3rd Party Monitoring Service and shall test the system response by tripping each of the alarm points in turn and validating the 3rd Party Monitoring Service logs with those recorded by the Central Operations Audit Trail log in conjunction with the Region’s representative.

  - Installation – Enterprise Software Integration

- Integrate or modify the configuration for the facility which being modified into the Region’s existing Enterprise software database.

- The Contractor shall co-ordinate the Work to incorporate the facility into the existing Enterprise system with the Region.

- This work shall be completed a minimum of 15 Working Days prior to the date of Substantial Performance of the Work.  The Contractor shall coordinate this integration effort with the Region’s Security and Life Safety Coordinator at 1-877-464-9675 ext. 76900 unless informed otherwise.

  - Operation - General

- Operation of the new security system is to function similarly to existing systems installed at other Regional facilities of a similar type.  The Contractor shall confirm all security system functions and operation with the Region of York Security and Life Safety Coordinator at 1-877-464-9675 ext.76900 prior to undertaking any programming unless otherwise informed.

- Overview: A general overview of the intended operation of the system is as follows:

  - The system shall allow for the monitoring of intrusion detection alarms inside the system alarm monitoring module, in addition to giving command and control of supported intrusion detection devices.  Once alarms are brought in to the system, they shall be stored in the system Audit Trail log.

  - All system events either designated as alarm conditions or not designated as alarm conditions shall be stored in the system Audit Trail log.

  - Each door shall be programmed to generate “Door Forced” and “Door Held Open” alarms.  These alarms shall have a user-definable, independent time delay which if not otherwise specified should be:

  - Time to trigger a “door held open” pre-alarm is 45 seconds;

  - Additional time for a “door held open” alarm is 10 seconds; and

  - Time to trigger “door forced “alarm is immediate.

  - Request to exit (“RTE”) motion sensors are to be installed on the interior of all perimeter exit doors which are equipped with door contacts in order to prevent false “forced entry” alarms caused by egress of personnel even when the security system is armed.  RTE’s (motion sensors) are to be configured to only shunt egress detection for 45 seconds unless otherwise specified.  RTEs shall not be configured to release the electric strike.  These RTE’s shall be aimed carefully so that that the sensor is not triggered by individuals or activities not related to exiting through the door, such as by individuals using a stairwell or a coffee machine close to the exit door.  The RTE described here will require a different configuration if the door is locked by an electro magnet.

  - Where access control and intrusion detection systems are installed on doors which also have automatic operators (also referred to as handicapped door operators), there are a number of special requirements.  In order to achieve these added functions, there needs to be a door interface relay / sequence board which can integrate and schedule operation of the inputs and outputs in a way that the security system cannot.  This device is normally installed in the ceiling above the handicapped door.  This device integrates some of the functions identified below and introduces delays as may be required to ensure that the door lock and the handicapped operator function in sequence and not simultaneously.  The usual sequence of operations is as follows.

- The card reader on the insecure side of the door is always active.

- The insecure side handicapped paddle is normally inactive.

- The door is normally closed and locked unless there is a schedule during which the lock is disengaged.

- The secure side handicapped paddle is normally active and there is also an RTE device (typically a motion sensor)

- When entering the secure space from the insecure side:

The user will swipe a valid card on the reader which will enable the insecure side handicapped paddle and unlock the door.  Those who are capable of doing so may open the door manually and enter through the door which will automatically close and relock behind that person.  Mobility challenged individuals may press the handicapped paddle which will activate the handicapped operator by activating the REN (Request to Enter) on the access control system.  Once the operator completes its cycle and closes the door the insecure side handicapped paddle will be inactive and the door will relock.

- When leaving the secure space and going to the insecure side:

The user will approach the door thereby activating the RTE device, thereby unlocking the door.  The door can be opened by pulling on the handle or by pressing the handicapped paddle to activate the door operator.  Once the operator completes its cycle and closes the door the secure side handicapped paddle will be active and the door will relock.

  - The security system shall automatically upload/download information to/from the control panels while the control panels are in communication with the host server application.  A data download/upload may also be initiated manually by a technician should this be required.  This transfer of data may consist of either controller database information or alarms and events.

  - Data transfer shall not interfere with normal daily operations.  The local system shall be capable of working for at least 24 hours or 5,000 events written to local logs without communications to the central system.  Alarms will sound locally and they and the events will be recorded locally when such downloads/uploads are unavailable.  Should the local storage capacity be exceeded the oldest records will be overwritten.  Once the downloads/uploads resume, these records will be transferred and will then appear in the Central Audit Trail log.

- Authentication to the security System shall be via programmed Access Levels, e.g., all users will have only the access levels which are predicted to be relevant to their responsibilities, and these may relate to only one site for a local responsibility such as a librarian, or to many sites for an ITS trainer.  When new sites are brought on-line, existing access levels may need to be augmented or new ones may need to be approved.  Such access levels can be further customised by using schedules to allow for the accesses to be limited by time of day or day of week, thereby providing more control and greater security.

- Proximity Card Reader and combination “Proximity Card Reader and Arming Button” shall function as a method of disarming and arming the security system respectively.

- When a valid card is presented to the Card Reader on the insecure side of the door, the system of which that reader is a part will disarm immediately and temporarily unlock the door.  The door does not need to be opened and even if the door is not opened the system will remain disarmed and the lock will relock after the timer expires.

- The security system shall only Arm if there are no open contacts, open areas, or alarms in the system.  Troubles will generally not inhibit Arming of the system, e.g., a low battery voltage causes a trouble signal which will not prevent arming of the system.  When the system is “secure”, i.e., “ready to arm” (as shown on the keypad), swiping the card at the Card reader on the secure side of the door and then pressing the arming button which incorporates a 45 second delay and will result in the system commencing a countdown timer, which will be set to 1 minute unless otherwise specified.  During this “Exit Delay” the keypad display will beep slowly and display “Exit Delay in Progress”.  When the “Exit Delay” is complete, the sounder will become silent and the “Ready to Arm” indication will be replaced with the “armed” LED status indicator at the keypad will be illuminated on the keypad.

- Upon presentation of proximity card with the correct Access Level, i.e., a valid access card, to a card reader, the security system shall activate the unlocking mechanism on the corresponding door, allowing that door to be opened.  As noted above this will happen when the security system area is armed or not.

- Upon authorized entry through a door (Access Granted) the system shall automatically disarm the security system area related to that door if it was previously armed.  “Security System Disarmed” status shall be indicated as an input to the access control and intrusion system.

- Prior to exiting from a facility, personnel shall arm the security system by presenting their card to the secure side “Arming” card reader and then pushing the adjacent push button (Arming Button).  This sequence of events will initiate arming of the security system.  “Security System Armed” input shall be signalled to field controller.  The system shall only Arm if there are no alarms or “open contacts” in the system.

- The use of a manual, “override” key entry to an armed facility, (or any other means of opening the door except for the use of an approved access card) shall cause “Intrusion Alarm” input to be signalled to the access control system and to the intrusion detection system.

- Upon a forced entry to the facility, “Intrusion Alarm” input will be signalled to the local access control system and the intrusion detection system.  The Central System maintains “Security System Armed” input signal to the access control system and intrusion detection system.

  - Security Wiring Field Quality Control

- Sensor and other signal wiring should be tested for continuity of each conductor using ohmmeter or DC buzzer.  Resistance values shall not exceed 5 ohms.  Megger or 120 Volt filament lamp testing is not acceptable.

- Carry out functional tests with the Region’s Representative to confirm field wiring, interconnections, and device functionality.

- Depending upon the magnitude and the complexity of the system, the Contractor may elect to divide the security system into logical sections, and activate one section at a time so as to sequentially verify the operation of each selected section.

- Upon completion of the sectional tests, the Contractor shall undertake testing of the integrated system comprised of all the sections.

- The Contractor shall verify operation of the complete system for operational sequencing.

- For local testing, each device/sensor should be tested and marked off one by one until all devices/sensors are tested.  Each sensor shall be verified to the intended zone.

- Submit one copy of all signed and dated test results to the Consultant.  This shall only be done after any aberrations uncovered during the testing have been rectified.

  - Network Wiring Field Quality Control

- The network cabling requires certification in order to achieve full acceptance by both the Region and the Manufacturer.

- The Region requires that the performance of the entire LAN infrastructure be certified to Category 6e performance which shall include at least the following parameters as defined in the ANSI/TIA/EIA-568-B.1 and other compatible standards by using a calibrated tester.

- Cable installers will generally provide these results for each cable link in tabular and graphical format which should be generated by the test equipment.  These results will automatically flag those measurements which do not meet the performance standards which were selected, e.g., Category 5, Category 5e Category 6, Category 6e etc.

  - Wire map

  - Propagation delay

  - Delay Skew

  - Cable Length

  - Insertion Loss

  - Return Loss

  - Near-End Crosstalk (NEXT)

  - Power Sum NEXT (PSNEXT)

  - The Equal-Level Far-End Crosstalk (ELFEXT)

  - Power Sum ELFEXT (PSELFEXT)

  - Attenuation-to-Crosstalk ratio (ACR)

  - Power sum ACR (PSACR)

  - DC Loop Resistance

- Naturally for the entire network to perform satisfactorily the components forming part of the network must all be certified to the same standard.  Patch cords in particular are generally purchased pre-manufactured and are not normally a part of the “link testing”.

- The system inspection shall include inspection of the labelling, the cable dressing, the terminations, the testing, patch panels, the jacks and the type of the insulation which has been used.  All of these items shall be accepted by the Region only if all components are certified to the same standard.

  - Warranty

- The entire passive network shall be accepted by the manufacturer after certification under its “lifetime warranty” program.

- The beneficiary of the Warranty shall be the Regional Municipality of York.

- The Contractor shall be responsible to ensure that installation complies with the warranty conditions.  The general requirements are that:

  - All components shall be from a single manufacturer.

  - The installation is performed by Factory Trained installers.

  - The installation is tested and certified to meet the required standard.

- During the Warranty period and as may be determined thereafter, the Region requires that the Contractor ensure that the service and repairs to the security system shall meet the following target service levels for the entire security system installed under the contract.

- Response Time, Repair Time and Overall System Availability

- The Contractor will respond to warranty work in reasonable time such that overall requirements for system availability are met.  Availability of replacement components will support a reasonable response time.  The Contractor shall be penalized when, during the warranty period, an incident involving a failure of any part of the system results in more than 48 hours of down-time or if the Contractor fails to commence warranty service within 12 consecutive hours from the first notification (being “Made Aware”) of the incident by York Region personnel or by system diagnostics.

- “Made Aware” means when the Contractor has been advised by any party or when detected by or should have been detected by the Contractor.  Additionally, the cumulative downtime shall not exceed 220 hours in any 6 month period or a penalty for each additional 24 hour period of downtime shall be applied.

- Failure of any part of the system is defined as, but not limited to, any loss of functionality, malfunction of the security system or failure to attain the performance requirements as defined in this specification, in the Contract Documents or described in the training provided to the York Region staff or any on-line terminal malfunction, or communications failure which is not the result of a utility company to provide their service, under normal usage, vandalism, or traffic damage.  These considerations clearly apply to the components which are referenced as the Security system or the surveillance camera system.

- The following table summarizes incident response times, incident repair times, and cumulative downtimes:

| Target Response | Response Time | Penalty Rate |
| --- | --- | --- |
| Maximum Time to respond to an incident | 24 hours | $250.00 per 24-hour period or portion thereof. |
| Maximum Time to repair problem causing an incident | 48 hours | $250.00 per 24-hour period or portion thereof. |
| Cumulative down time during any 6-month period | 220 hours | $250.00 per 24-hour period or portion thereof. |

- The Contractor shall submit system Diagnostic Reports to the York Region Security Coordinator on a monthly basis throughout the warranty period within 14 days of each month end.  These reports shall validate the performance during the previous month and certify compliance with the performance and up time requirements.

- The Contractor shall make available qualified technical support during normal working hours and emergency support at all times 24 hours a day for each day throughout the warranty period.

  - Close Out

- Close Out of the project shall require that the some or all of the following documents and miscellaneous items shall be provided to the Region, addressed to the Security Project Coordinator, via e-mail or to 145 Harry Walker Parkway, Newmarket, ON, L3Y 7C5.

- One copy of all signed and dated test results as approved by the Consultant.  This shall only be done after any aberrations uncovered during the testing have been rectified;

- A written list of all passwords, keywords, serial numbers and/or configurations that were encountered during the installation of the operating system and application software;

- Assignment of all warranties, licences and product registrations to the “Regional Municipality of York” and documentation to this effect;

- Ensure that any permits or temporary configurations of any kind are returned to their permanent “operational” status and appropriate documentation is provided confirming this status;

- All installation software, user manuals, accessory cables, calibration units and any other material accompanying the installed equipment; and

- All keys, special tools, spare parts, unused components, permits, approvals, as-built drawings and project related documentation.

- All documentation shall be provided in both hard copies and also in soft copies (using bother source document format and PDF format).  Source documents shall be in AutoCAD or Word format.  There shall be no locks, keys or restrictions preventing the use of these documents by the Region and the documents shall be certified to be free of viruses or other malware of any kind.

  - Wiring Identification

- Identify all wiring infrastructure including fibre optic cabling and conduits with wire markers in accordance with the requirements and guidelines of Appendix V: “Labelling Requirements”.

- Identify each conductor, including any spares, with a unique alphanumeric designation to facilitate troubleshooting and maintenance as identified by Region of York standards.

- Identify all controller wiring at terminal blocks and connection points with the controller terminal (I/O) address numbers.

  - Site Testing

- Following installation or modification of the security System at a facility, Site testing shall be performed by the Contractor.  Testing is to be co-ordinated with the Region.

- Record test results in a log book and submit to the Consultant for reference and approval.  Replace or repair circuits which do not meet requirements before submitting to the Consultant.

- The Facility is to be tested to confirm/demonstrate the proper operation of the System in accordance with a test plan approved by the Consultant.

- The Region’s representative is to be present for all final testing.  The Region’s representative is to confirm that testing has been satisfactorily completed and that the system is ready for operational use as intended.

- All exterior facility access doors are to be tested for valid access control functions and intrusion detection operation while using test proximity card(s).  The corresponding inputs to the SCADA system are also to be verified when they are present.  The security system is to be tested with both valid and invalid proximity cards in online and offline operating modes.  The testing shall ensure that both the mechanical and electronic aspects of the doors as well as any other special features function correctly.  The various trouble options shall also be shown to work properly.  Any malfunctions must be corrected prior to the Region accepting the system.

- Use of the “emergency” mechanical key override through all perimeter doors is to be tested by manually opening such doors.  The key must readily provide access without any action by the access control system but must also report the key operation as a “Door Forced” event.  Corresponding inputs to the SCADA system are to be confirmed as may be appropriate.

- Since all arming is activated by use of a card and push button at one of the doors in each facility, there needs to be a careful verification of this function at each door which is equipped with this function.  The testing shall ensure that any of the “faults” intended to inhibit the arming function do prevent the arming and that these situations are clearly identified on the keypad screens.  Such faults include, door open, trouble events, inadequate credential access level, communications failure etc.  The testing process requires comparison of the Audit Trail log with the local record maintained by the testing team.

- All event and alarm conditions are to be verified and logged to the system Audit Trail log.  The activation of such alarms and associated events are to be logged using an accurate time source, e.g., a cell phone and then recorded.  There are several different responses which should be initiated by this testing process and which therefore require testing:

- A local response, e.g., siren at the door,

- A facility wide response, e.g., an active icon on the alarm management screen in the facility,

- A Regional central monitoring operation notification, e.g., an active icon on the alarm management screen; and

- Notification to the 3rd Party, off site Monitoring Station.

- Upon completion of the on-site testing, the “test team” records shall be compared with the system Audit Trail log report and with the notification log which shall be obtained from the 3rd Party Monitoring Station.  Any evidence of a malfunction in this auditing process needs to be corrected before the Region will accept the system.

- Following successful integration with the Region’s Security Server, “shift programming”, otherwise referred to as “access level adjustments” of the facility, if applicable, are to be coordinated through the Region’s Security and Security Systems Administrator who is available at 1-877-464-9675 ext.76900.

- APPENDICES

- LIST OF APPENDICES

| Appendix | Contents |
| --- | --- |
| A | Regional Security System Naming Convention Standards |
| B | Regional Approved Commissioning Form |
| C | Standardised Terminology |
| D | Standards Applicable to Regional Security Projects |
| E | Standardised Security Configurations |
| F | Procedure for Equipment Substitution |
| G | Standardised Abbreviations |
| H | Environmental Requirements |
| I | Access Control System Value Added Resellers |
| J | List of Approved Security Equipment |
| K | Approved Access Control Equipment |
| L | Approved Intrusion Detection Equipment |
| M | Approved Intercom Equipment |
| N | Approved Credential and Credential Reading Equipment |
| O | Miscellaneous Security Devices |
| P | Digital Video Management System |
| Q | Conduits, Fittings and Accessories |
| R | Cabling, Conductors and Miscellaneous Accessories |
| S | Parking Barriers |
| T | Locks |
| U | Universal Washroom |
| V | Labelling Requirements |
| W | Sample Graphic Map, Regional Layout and Icons |

  - Appendix A – Regional Security System Naming Convention Standards

All components and interconnections are to be identified by a unique name which shall be used on drawings, documentation and labels.

These names are to be assigned in compliance with the following guidelines.

Labels are to be attached in a manner which is durable, can be readily read and are in accordance with these guidelines and is further documented in Appendix V.

A full list of the Sites and existing buildings can be provided on request.  The Contractor is advised to obtain the latest listing to ensure that this contains any recent updates.

Site:

E005-B (Facility/Building Code)	E = Municipality (example: East Gwillimbury)

followed by address	005 = Building Site Sequential Number

and/or building name	B = Identifies site as an owned Building

Other options:

L = Leased Building

P = Property

System Controllers and Panels (Lenel LNL-2220, Bosch B9512G):

E005SS01 (LNL-2220)	E005 = Site Number

E005SI01 (B9512G)	S = Security controller

S = Intelligent System Controller (ISC)

I = Intrusion Alarm Panel (Bosch)

01 = ISC/Intrusion Panel Sequential Number

Door:

E005D001	E005 = Site Number

D = Card Reader/Door

001 = Matches Reader Port it is associated with.

  - Appendix B – Regional Approved Commissioning Form

The commissioning procedure is described in the Specification Document, Section1.6 Testing and Quality Assurance.

The appropriate Commissioning Forms are to be completed and submitted to the York Region Project Manager for approval no later than 48 hours prior to the proposed commissioning.  The Contractor is responsible to ensure that the forms correctly identify the quantity and description of the elements which are associated with a particular project.  Note that the forms are available in Excel format and should be submitted in that format.  There are 3 forms, one provides the Legend which is to be used and the Overall Project Summary, the second provides a record of the Individual Security Devices and the third form identifies changes to the video surveillance system.  The sample forms are to be replaced by those included with the contract documents.  Additional copies of these forms shall be created as may be required.

The contractor shall obtain copies of these forms directly from the Region so as to ensure that the forms being used reflect the latest version of the forms and incorporate the latest updates and reflect any technology changes.

  - Appendix C – Standardised Terminology

ACCESS CARD is generally a plastic card, the size of a standard Credit card, with a chip or magnetic stripe containing encoded data that is read by passing the card through or over an electronic device which in turn transmits the encoded data to an electronic controller.  From this data the controller identifies the card user and allows or denies access to restricted or secure areas or systems.  There any many different forms of card encoding and card reading in common use.

ACCESS CONTROL see Access Control System.

ACCESS CONTROL SYSTEM is an electronic system which controls the status of control locations in accordance with the rules and inputs which have been programmed.

ACCEPTANCE is the process by which the security system is deemed to have passed the Commissioning test and when required the Burn-In testing.  The Warranty period will then commence.

ALARM is the name given to the Intrusion Detection System status when a situation occurs which requires immediate on-site investigation, generally because of an unauthorised entry or because a sensor has notified the detection system of an unacceptable status.  An Alarm may originate from either the Access Control System or from the Intrusion Detection System.  The nature of the alarm notification is not defined and can be a loud siren, stroboscopic lights, electronic messaging or any combination of these and other alternatives.  The IDS is normally expected to provide a sequential time stamped log to allow for forensic investigations following an alarm.

ALERT is a low priority notification which may originate from either the Access Control System or from the Intrusion Detection System.  Alerts are normally activated in order to “alert” security staff that something is not “quite as expected” and may in some cases be followed by an Alarm when the status has extended from “not quite as expected” to “seriously out of order”.  As examples consider that

- The temperature in a food freezer has warmed from -20°C to a threshold of -10°C at which temperature an alert is signalled and when the temperature rises to -3°C, an Alarm is signalled.

- An access-controlled door is held open for 2 minutes longer than the programmed “opening time” causing an Alert to be issued and sound locally but if the door remains open for 4 minutes longer than expected, the Alarm will be activated.

- If the “panic alarm” is activated by a staff member in a washroom or at a service counter there will be no alert, but the Alarm will immediately be activated.

- As soon as the power fails in a building an alert will be issued but the alarm will only be issued when the failure has lasted for, say 2 hours.

ASSETS are tangible or intangible things of the Region of York.  Assets include but are not limited to information in all forms and media, networks, systems, material, real property, financial resources, employee trust, public confidence and reputation.

ATTACK is any action to execute a threat.

AUTOMATIC DOOR OPERATOR is a motorised device used to activate a door thereby allowing those with restricted strength or mobility to open doors which might otherwise be too heavy.  These are also referred to as Handicapped Door Operators although this term is generally no longer used.

AVAILABILITY is the condition of being usable on demand to support operations, programs and services.

BACnet is a communication protocol for Building Automation and Control (BAC) networks that leverage the ASHRAE, ANSI, and ISO 16484-5 standard protocol.  BACnet was designed to allow communication of building automation and control systems for applications such as heating, ventilating, and air-conditioning control (HVAC), lighting control, access control, and fire detection systems and their associated equipment.

BASE BUILDING SECURITY is a description of the security safeguards provided to protect a facility but not the necessarily the assets contained in the building.  Basic building security provides a base or starting point for other security requirements (i.e., minimum and enhanced safeguards) to be added to protect the specific assets held by the facility.  This is dependent on a TRA and a specific business requirement.

BASELINE SECURITY REQUIREMENTS are the mandatory provisions of the Region of York and its associated operational standards and technical documentation.

BINARY DIGIT is the smallest unit of data in a computer and is often abbreviated to “bit”.  A bit has a single binary value, either 0 or 1 (see also Byte).

BITS PER SECOND is the speed of data transmission measured in bits per second and is often referred to as “baud”.  Network speeds are generally measured in bps and have risen sharply with a tenfold increase for each new technology ranging from 1 Mbps through 10, 100 Mbps and 1Gbps and 10 Gbps.

BOND SENSOR see Hold Force Sensor.

BURN-IN TESTING is an extended form of “in service” System Integration Testing.  For the period which has been defined for this test the system shall be left operational and shall endure all normal in-service characteristics.  This may include power outages, weather extremes, etc.  The Burn-In Test is designed to prove the operational capabilities of the entire system.  This test may, therefore, require that the system function through a normal range of weather and perform in the manner which is expected for a minimum of 30 days.  Thus, some burn-in tests can only be performed during the summer or during the winter seasons.  No adjustments, configuration changes or maintenance of any kind should be performed during this period.  The details of the BIT which is to be performed shall be noted in the Contract Documents.

BUSINESS CONTINUITY PLANNING is an all-encompassing term which includes the development and timely execution of plans, measures, procedures and arrangements to ensure minimal or no interruption to the availability of critical services and assets.

BY-PASS indicates that either one or more sensors or zones are by-passed or off-site monitoring has been “disabled”.  While all of these options are generally invoked during testing, the purpose in all cases is to allow for the testing of an alarm system without activating a response from security agents responsible for such investigations.  In some situations, if the security system is malfunctioning and the problem has been reduced to a particular sensor or zone, the sensor or zone may be bypassed to allow the remainder of the system to function normally pending the repair of the defect, a by-passed sensor or zone does not provide any signalling.  If the entire security system is by-passed, the monitoring service will not activate any response plan for the duration of the “by-pass”.  It is common practice, in these circumstances for the monitoring service will provide a detailed listing of all the alarms received to the client so that the client or the security contractor can compare the report with the stimuli applied to the security system.

BYTE consists of a number of bits and has generally been associated with 8 bits leading to its common nomenclature of an “octet” and allowing for values from 0 to 255.  Most modern computers use 4 or 8 bit “words” yielding 32-bit or 64-bit architectures.

BYTES PER SECOND or the number of bytes transmitted per second.  There are commonly 8 bits per byte so that a speed of 110 baud is equivalent to approximately 10 characters per second when allowing for parity and other error correction bits.

COMMON ACCESS CARD is a term describing the particular form of access card used by all US Government and military personnel.  It should not be confused with any other form of commonly used access cards.

CBRN a general term covering attacks using “Chemical”, “Biological”, “Radiological” or “Nuclear” weapons.

CBRNE this term adds “Explosives” to the possible threats (see CBRN).

CLOSED CIRCUIT TELEVISION, often referred to as “Surveillance”.

CENTRAL STATION see Monitoring Station.

CIVIL DISTURBANCES Means acts of violence and or disorder prejudicial to the public law and order.  Civil disturbances most often arise from political grievances, urban economic conflicts, community unrest, terrorist acts, or foreign influences.  They can range from peaceful picketing to full-blown riot situations.

CODE can refer to the most recent enacted version of any of a number of Codes which govern the construction and operation of buildings and systems.  Typically, the pertinent Codes will include at least the Ontario Electrical Safety Code, the Ontario Building Code, the Elevator Code and the Fire Code.

COMMISSIONING describes the activity of commissioning which is the measured process of placing the security system into its initial operation and may include Proof of Performance and System Integration Tests sufficient to demonstrate the operational status of the entire system under operating conditions.  Following the completion of the Commissioning process, the security system shall, if required, complete the Burn-In testing to qualify for Acceptance.

COMPROMISE is the unauthorized disclosure, destruction, removal, modification, interruption or use of assets.  Also used to classify the unauthorised opening of a portal, door etc. i.e., an intrusion.

CONTACT ID is the number of the Monitoring Station information in the security system reference list of numbers and alternatives to be called when notification of an alarm is to be transmitted.

CONTINUOUS LIGHTING consists of a series of fixed lights arranged to flood an area continuously with overlapping cones of light.

CONTRACT DOCUMENTS are the documents describing the construction project and the responsibilities of the parties to the agreement.  Generally, these documents will include either a detailed design including drawings or may define the performance requirements thereby requiring the contractor to perform the detailed design.  In some construction projects the contract documents may include work to be performed by more than one discipline and in other circumstances the project work relates to only a single discipline.

CONTROL OF ACCESS describes the process of ensuring authorized access to assets within a facility or restricted areas by screening visitors and material at entry points by personnel, guards or automated means and, where required, monitoring their movement within the facility or restricted access areas by escorting them.

CRIME PREVENTION THROUGH ENVIRONMENTAL DESIGN defines territories and how they are controlled and managed based on the use of “concentric rings of control and protection.”  Outermost rings are supported by additional inner rings of protection.  Each of these concentric rings will be addressed as layers of protection within these guidelines and are intended to sequentially deter, deny access to, and slow down possible malefactors.

CREDENTIALS are a means of identifying a user in to order to manage the “privileges” accorded to that individual.  The most common credential is an access card but other credentials technically include keys (mechanical or electronic), fobs (with microchips), voice signatures, finger prints, retinal patterns, hand geometries and other evolving technologies.  Credentials are used both in Physical Security settings (doors, windows etc) and in Cyber Security settings (remote access, banking etc).

CANADIAN STANDARDS ASSOCIATION is the Author and Authority who originate the standards, (including the Ontario Electrical Safety Code), which govern most of the devices, particularly the electrical devices used in Canada.  The CSA symbol (or approved equivalent) must be permanently attached to every electrical device used with any regular power supply.

CATEGORY 4, 5, 5e, 6 etc define the performance of unshielded twisted pair (UTP) ethernet cables as specified by the Standards developed by the ISO/IEC and ANSI/TIA/EIA 568.  These standards define the cable length as limited to 90m (300 ft), a characteristic impedance of 100 ohms.  The cable Categories have increased in ordinal and in performance in response to network demands moving from 10 Mbps to 100 Mbps to 1 Gbps to 10 Gbps and rendering older wiring systems obsolete.

CYBER SECURITY is the practice of defending computers, servers, communications links, mobile devices, electronic systems, networks, and data from malicious attacks.  It is also known as information technology security or electronic information security.  This is quite distinct from Physical Security which is the focus of this document.

DETECTION refers to the use of appropriate devices, systems and procedures to signal that an attempted or actual unauthorized access has occurred.

DIN RAIL is a commonly used device for mounting many types of modules inside enclosures.  It was originally specified by the Deutsches Institut für Normung (DIN) in1928 and has since been adopted internationally (Top Hat Rail IEC/EN 60715).

DOCUMENTATION shall include shop drawings, catalogue sheets, calculations, drawings, diagrams, test print outs, photographs or/and text.  Specific references may limit the particular documentation to specific criteria.  All documentation submitted to the Owner shall be in English.  The format of the Documentation shall be in accordance with the requirements as specified in the Contract Documents.

EMERGENCY LIGHTING depends on alternative power sources, and therefore, is reserved for times when regular lighting is not available.  Typically, such lights are selected luminaires or fixtures which are selected from the continuous lighting fixtures and which are provided with an alternative source of power.

END OF LINE or END OF LINE RESISTOR refers to the placement of one or sometimes more than 1 resistor at the remote end of the sensor communications line.  See Supervision for more details.

ENVIRONMENTAL THREATS refers to natural phenomena/disasters that have the potential to damage resources or services or to interrupt activities or operations, e.g., hurricanes, floods, heat waves.

EXPLOSION PROOF refers to the certification required of electrical and related safety devices used in hazardous locations.  In electrical and safety engineering, hazardous locations are places where particular fire or explosion hazards may exist.  Sources of such hazards include gases, vapours, dust, fibres, and airborne particles, which are combustible or flammable.  Electrical equipment installed in such locations could provide an ignition source, due to electrical arcing, or high temperature.  Standards and regulations exist to identify such locations, classify the hazards, and design equipment for safe use in such locations.

EXTERNAL THREATS refer to threats to the integrity and security brought about by individuals or circumstances outside of the Region of York.

FACILITY - a physical setting used to serve a specific purpose.  A facility may be part of a building, a whole building, or a building plus its site; or it may be a construction that is not a building.  The term encompasses both the physical object and its use (for example, weapons ranges, agriculture fields).

FAIL OPEN indicates that a failure of the control system will lead to the door or portal being uncontrolled and unlocked.  See FAIL SAFE for a further discussion.

FAIL SAFE is a term which may be confusing to the casual user as the term “SAFE” may relate to a portal (door) being “safe for humans”, i.e., open or “safe for property”, i.e., closed.  The terms, “FAIL OPEN” and “FAIL SECURE” are less ambiguous and therefore preferred.  The reference to “FAIL” refers to the state assumed by the door or portal when control is lost, e.g., when the power has failed, a cable is cut or software malfunctions.  It should be noted that while the establishing of a desirable “FAILURE” mode is desirable, unforeseen circumstances may prevent this mode being achieved, e.g., when a mechanical component seizes up or breaks.

FAIL SECURE indicates that a failure of the control system will lead to the door or portal being uncontrolled and locked.  See FAIL SAFE for a further discussion.

FALSE ALARM refers to alarm systems being triggered by something other than the expected trigger-event.  Examples of those applications include residential burglar alarms, smoke detectors, industrial alarms, and signal detection theory.  False alarms are, correctly, limited to those alarms caused by a system not behaving in accordance with the system programming, e.g., a smoke detector activated by dust, a motion sensor activated by a mouse, s glass shock sensor activated by a tree branch hitting the window.  (See Nuisance Alarm).

FALSE ALARM RATE, is defined as the number of false alarms (in which an alarm, or warning, is given in spite of a non-event) per the total number of ‘non-events’ (times the event didn’t happen).  A false alarm rate is also known as the probability of false detection.

FALSE ALARM RATIO, is the number of false alarms (in which an alarm, or warning, is given in spite of a non-event) per the total number of warnings or alarms in a given study or situation.

HAZARDOUS LOCATIONS refer to electrical and safety engineering locations  where fire or explosion hazards may exist.  Sources of such hazards include gases, vapors, dust, fibers, and air borne particles, which are combustible or flammable.  Electrical equipment installed in such locations could provide an ignition source, due to electrical arcing, or high temperature.  Standards and regulations exist to identify such locations, classify the hazards, and design equipment for safe use in such locations.

HOLD FORCE SENSOR (also referred to as a “Bond Sensor”) is a Hall Effect device mounted in an Electromagnetic lock to monitor the force between the solenoid (coil) and the armature (steel plate).  This force which is frequently either 600 lbf (3,000 N) or 1,200 lbf (5,300 N) diminishes rapidly if there is an accumulation of dirt (e.g., rust) on the surface or any other obstacle which prevents the 2 components mating properly.  The Hold Force Sensor (HFS) can detect any such holding force reduction and initiate an alarm indicating that the door is closed improperly.

INSIDER THREATS refers to trusted persons, possibly employees of the Region of York, who have been granted access to secured resources or services but could have ulterior motives.

INTERNATIONAL STANDARDS ORGANISATION which defines standards of many kinds and which are implicitly used by the national standards organisations such as CSA etc.  These international standards are crucial for example to allow for communications or for manufacturing.

INTEGRITY refers to the accuracy and completeness of assets, and the authenticity of transactions.

INTRINSICALLY SAFE is a protection technique for safe operation of electrical equipment in hazardous areas by limiting the energy, electrical and thermal, available for ignition.  In signal and control circuits that can operate with low currents and voltages, the intrinsic safety approach simplifies circuits and reduces installation cost over other protection methods.  Areas with dangerous concentrations of flammable gases or dust are found in applications such as petrochemical refineries and mines.  As a discipline, it is an application of inherent safety in instrumentation.  The alternative to using Intrinsically Safe techniques is to use equipment which is certified as “Explosion Proof”.  High-power circuits such as electric motors or lighting cannot use intrinsic safety methods for protection.

INTRUSION DETECTION SYSTEM is a system to monitor, detect and notify unauthorised access or the deviation of sensor observations from acceptable values, e.g., a door which has opened with the presentation of an approved credential or a motion sensor detecting movement in a room which is thought to be closed.

LATCH or LATCHING relates to a lock being set electronically to simulate a “latched door”.  In this mode the door is insecure and can be opened without using credentials.  The status change may be automated, as in the scheduled opening of an office main entrance, may occur as a result of a manual action at the system console or may be activated by a specially authorised credential.

LOCAL AREA NETWORK is a computer network that interconnects computers within a limited area such as a residence, school, laboratory, university campus or office building.  In such an environment the single network can be managed and it is often true that all of the computers belong to a single person or entity, thereby providing for enhanced security.  Similarly, the network infrastructure generally all belongs to the same entity thereby ensuring adherence to the same technical criteria.

LOCKDOWN can be used to protect people inside a facility or, for example, a computing system, from a threat or other external event.  In buildings, doors leading to the outside are usually locked so that no person may enter or exit.  A “full lockdown” usually means that people must “stay where they are and may not enter or exit a building or rooms within it, needing to go to the nearest place designated safe if not already in such a place.”  Lockdowns can be defined as “Exit permitted”, “Entrance permitted” or “Full lockdown” thereby defining how access cards will function during the emergency.

MAINTENANCE CONTRACTOR means the Contractor who, following the supply and installation of the Security System, will be responsible for the Maintenance or Modification of the system.

MATERIAL- any tangible object with the exclusion of those embodying information.

MATERIAL SAFETY DATA SHEETS, have been renamed to SDS, Safety Data Sheets (See Safety Data Sheets).

MEAN TIME BETWEEN FAILURES is the predicted, mean or average elapsed time between inherent failures of a mechanical or electronic system, during normal system operation.  This is usually measured in hours, days or weeks.  The term is used for repairable systems.

MEAN TIME TO FAILURE denotes the expected time to failure for a non-repairable system.  Because Mean Time to Failure is relevant only for assets and equipment that cannot or should not be repaired, MTTF can also be thought of as the average lifespan of an asset.  This is usually measured in hours, days or weeks.

MEAN TIME TO REPAIR is a measure of the maintainability of a repairable item, which tells the average time required to repair a specific item or component and return it to working status.  It is a basic measure of the maintainability of equipment and parts.  This includes the notification time, diagnosis and the time spent on actual repair as well as other activities required before the equipment can be returned to service.  This is usually measured in hours, days or weeks.

MONITORED is to watch for or detect a breach of security.

MONITORED CONTINOUSLY is to confirm on a continuous basis that there has not been a breach of security.  Examples include electronic intrusion detection system, or someone guarding a particular point on a constant basis.

MONITORED PERIODICALLY is to confirm on a regular basis that there has not been a breach of security.  The frequency and diligence of monitoring is based on the recommendations of a Threat and Risk Assessment.  Examples of monitoring periodically include by means of a guard patrol, or through employees working at the location.

MONITORING STATION is the contracted agency to who all alarms which have been programmed for external notification are sent.  The monitoring station will then follow the Response Plan provided by the customer for each Reporting ID which may include calling phone numbers until a contact is reached or dispatching suitable response personnel.

MULTI MODE FIBRE is a type of optical fibre mostly used for communication over short distances, such as within a building or on a campus.  Multi-mode links can be used for data rates up to 100 Gbit/s.  Multi-mode fibre has a fairly large core diameter that enables multiple light modes to be propagated and limits the maximum length of a transmission link because of modal dispersion.  (See also Single Mode Fibre).

NORMALLY CLOSED identifies that when a momentary switch is not actuated, it is in its “normal” state.  Similarly, a relay is in its “normal” state when it is NOT powered.  Depending on how the device is constructed, its “normal” state can be either an “open” circuit or a “short” circuit.  When a contact is “open” until the button is actuated, it's said to be “normally open” (abbreviated NO) and conversely when the contact is “closed” until the button is activated it is said to be “normally closed” (abbreviated NC).  Unfortunately, the security industry has corrupted these explanations and, for example, a door contact’s normal state is defined by the status of the door, i.e., the “normal state” of the door corresponds with the door being closed at which time the door contact is “energised” by the magnet or by the door and is referred to as “normally closed” although, in its “at rest” or normal state, the contact will generally be “open”.  The lesson is that the function of normally open and normally closed contacts must be reviewed with caution and varies by specific trades.

NORMALLY OPEN identifies that when a momentary switch is not actuated, it is in a “normal” state.  Depending on how the button is constructed, its normal state can be either an “open circuit” or a “short circuit”.  When a contact is open until actuated, it is said to be “normally open“ (abbreviated NO).  Unfortunately, the security industry has corrupted these explanations and, for example, a door contact’s normal state is defined by the status of the door, i.e., the “normal state” of the door corresponds with the door being closed at which time the door contact is “energised” by the magnet or by the door and is referred to as “normally closed” although, in its “at rest” or normal state, the contact will generally be “open”.  The lesson is that the function of normally open and normally closed contacts must be reviewed with caution and varies by specific trades.

NUISANCE ALARM is intended to reflect the correct operation of a security system which is however triggered by the incorrect operation of the system without any malicious intent, e.g., furniture movers wedging doors open so that they can work more quickly, opening a window in an already secured area, i.e., such alarms are reporting correctly but the cause is generally “human error”.

ONTARIO ELECTRICAL SAFETY CODE, the Canadian Electrical Code as modified and approved for use in Ontario.  This modification is generally enacted about 18 months following the issue of the CSA electrical code.

OPEN SYSTEMS INTERCONNECTION, (ISO 7498) a joint ISO and ITU-T standard for computer networks and communication protocols.  The OSI model, is a 7 layered description for communications and computer network protocol design, (Physical, Data Link, Network, Transport, Session, Presentation, Application).

OPERATIONS AND MAINTENANCE shall mean all services and materials necessary for the functioning of the ACS and IDS Systems.

PHYSICAL SECURITY refers to the use of physical safeguards to prevent or delay unauthorized access to assets, to detect attempted and actual unauthorized access and to activate appropriate responses.  This may be amplified to describe security measures that are designed to deny unauthorized access to facilities, equipment and resources and to protect personnel and property from damage or harm (such as espionage, theft, or terrorist attacks).  Physical security involves the use of multiple layers of interdependent systems that can include CCTV surveillance, security guards, protective barriers, locks, access control, perimeter intrusion detection, deterrent systems, fire, and other systems designed to protect persons and property.

PHYSICAL SECURITY ASSESSMENT REPORT which is essentially equivalent to a Threat and Risk Assessment report and is generally provided prior to designing a security solution.

PLENUM RATED is a designation used in conjunction with cable insulation.  Code requirements demand that any cable placed without suitable conduit in an air return plenum, such as is commonly done, shall have a low smoke generation capability.  Such cables are said to Plenum Rated, FT-6 or CMP certified.  (See Riser Rated)

PRE-INSTALLATION TESTING includes all testing undertaken prior to the installation of equipment and may also include testing of mock-ups, prototypes and normal factory production testing.  This is generally required for any New Equipment, i.e., equipment which is specially manufactured, but may be waived for Standard Equipment, i.e., equipment which is production manufactured.

PREVENTIVE MAINTENANCE (or preventative maintenance) is maintenance that is regularly performed on a piece of equipment or on a system to lessen the likelihood of failure.  It is performed while the equipment is still working so that it does not break down unexpectedly.  For example, door closers are required to ensure that doors close properly after a controlled entrance but may need inspection and adjustment to ensure that the air pressure from the HVAC system does not impact this function during seasonal changes.

PROBABILITY OF DETECTION is used in to establish the capability of a system to detect intrusions.  The use of analytics in combination with CCTV and other sensors are known to have some limitations and therefore to sometimes fail to provide alarms or alerts when expected.

PROOF OF PERFORMANCE TESTING includes all testing undertaken following the field installation of equipment to verify the physical and operational features of each item of equipment and each sub system.  This is required for all equipment.

PROTECTION in the context of physical security means the use of physical, procedural and psychological barriers to delay or deter unauthorized access, including visual and acoustic barriers.

PROVEN EQUIPMENT shall mean equipment, other than specified in the project specifications which has been supplied and installed by the vendor for a different but similar purpose.  To comply with this definition, the equipment shall have been installed, in at least, five sites in the last ten years, currently be operational and references shall be available from such Agencies.

RACK UNIT is a commonly used measure of height or width when referencing 19 or 23 inch electronic equipment racks as well as the modular equipment installed in them.  It is defined in the IEC 60297 as 1.75 inches (44.45 mm) so that a full height rack is often referred to as 42 RU or 42 U high, i.e., 6 ft 1.5 ins (1.8669m).

RECOVERY is the term used to describe the restoration of full levels of service delivery following an interruption in such service.

REPORTING ID is the internally programmed number identifying the location and nature of the alarm and which forms part of the information sent to the Monitoring Station.

RESPONSE is the implementation of measures to ensure that security incidents are reported to appropriate security officials and that immediate and long-term corrective action is taken.

RESPONSE PLAN is the document provided by the client to the Monitoring Station which identifies the action to be taken by the Monitoring Station for each of the Reporting ID’s.  Typically, the response plan will provide alternatives to address urgent situations if certain individuals are not available.

RESTRICTED, when applied to an Access Area, describes areas where access is limited to authorized individuals and generally includes Operations, Security and High Security Zones.

RISER RATED cables may be used without conduit in fire rated risers or riser rooms but may not be used in air return plenums where the smoke which the insulation would generate under fire conditions would be hazardous.  Such cables are referred to as Riser Rated, FT-4 or CMR.

RISK is the measure of probability of a particular mode of “attack” by an intruder to be successful in gaining entry.  It may also be summarised as the chance of a vulnerability being exploited.

SAFETY DATA SHEETS are required to provide information regarding all the potentially dangerous chemicals which may be on site as well as the required emergency procedures to be followed in the event of a misadventure.  See Material Safety Data Sheets.

SECURITY CONTRACTOR will be the Contractor providing and installing the system described in this Specification and who is trained and certified on the equipment which is being installed under this project.

SENSOR is any device used to monitor a parameter which provides remotely monitored information, e.g., door contact, glass break sensor, water leakage sensor, power failure or motion sensor.

SIMPLE APPARATUS is considered not to appreciably affect the safety of an Intrinsically Safe system. This apparatus is exempted from the requirement for certification.  The simple requirements are clearly specified in the apparatus standard.  “Simple Apparatus” should always be readily demonstrable to be adequately safe.  The usual examples of “Simple Apparatus” are switches, thermocouples, resistive temperature detectors and junction boxes

SINGLE MODE FIBRE is a fibre optic cable which has a smaller diameter core than the Multi-Mode Fibre and allows only one mode of light to propagate.  Because of this, the number of light reflections occurring as the light passes through the core decreases, lowering attenuation and creating the ability for the signal to travel further.  This application is typically used in long distance, higher bandwidth runs by Telco’s, CATV companies, and Colleges and Universities.  (See also Multi Mode Fibre).

STANDARD EQUIPMENT see PROVEN EQUIPMENT.

STAND-BY POWER is often a generic term referring to the availability of both a short term, battery-based power source designed to last for a brief period (see Uninterruptible Power Supply) and also a longer-term power source which may be from a local generator or an alternative feeder from a sub-station or transformer.

STRUCTURED CABLING is the communications cabling architecture defined by standards so that the cabling can be maintained and the associated networks can be modified and upgraded as may be required.  This architecture defines 6 components, Entrance Facilities, Equipment Rooms, Backbone Cabling, Horizontal Cabling, Telecommunications Rooms (or Enclosures) and Work Area Components.

SUBSTITUTION is the process of requesting and justifying the use of equipment other than that specified by the project specifications.  The contractor may request the substitution but must follow the process for submission and justification of the alternative equipment.  The Region of York is the final arbiter with regard to the request for a substitution.

SUPERVISION is the term given to the use of resistors in different configurations to monitor the connections between remote sensors and the panels to which they are connected.  Most sensors switch between “open” and “closed”, i.e., between “infinite resistance” and “zero resistance”, when they change state.  By placing resistors in series and in parallel with the “sensor”, the system will generate alerts if the wires are cut, shorted or the resistance measured by the terminating panel differs from the expected configuration.  This supervision ensures that any “tampering” with the infrastructure will be identified and the alarms triggered by such situations are generally referred to as “tamper alarms”.  See TAMPER ALARMS.

SUPERVISORY CONTROL AND DATA ACQUISITION protocol and associated equipment which is used, particularly in association with the water and waste water equipment used by the Region and which is interconnected with the security system.  Many of the devices or parameters associated with the monitoring of water and waste water relate to analogue data such as temperature, pressure and flow rates as opposed to most security monitoring which is digital, i.e., the door is open or it is closed.

SURREPTITIOUS ATTACK is a secret unauthorized attack to breach or circumvent a defensive system or some of its components in such a manner that the custodians and/or security force cannot readily detect the attack.

SURVIVABILITY is the ability for the equipment to be subjected to the conditions which are referenced for an indefinite period without being operated and then returned to normal operation under different conditions without suffering any degradation or damage, e.g., keeping electronic equipment in a storage facility which is at -40°C when the operational requirement might call for a minimum to -20°C could affect the equipment survivability.

SYSTEM INTEGRATION TESTING includes all testing required to verify the harmonious operation of all designated subsystems.  In the case where the larger system consists of individually approved sub components, partial testing shall be carried out on selected samples of equipment only.

TAMPER is the general process of attempting to make unauthorised modifications to a security system, generally in order to defeat the system’s ability to detect a planned intrusion.  The term “tamper” is often used colloquially to refer to a “tamper switch” which is contact attached to an equipment panel door to detect any unauthorised opening of the cabinet, i.e., tampering with the equipment.

TAMPER SWITCH see TAMPER

TEST REPORT is a pre-programmed call made from the Client site to the Monitoring Station, typically once per day and generally during “silent hours”.  The Reporting ID is defined as a “Test Report” and the Response Plan will confirm that no action is required.  If the scheduled Test Report is not received, the Monitoring Station will typically generate a notification to the Client indicating the absence of the Test Report at the agreed upon scheduled time.

THREAT The perceived imminence of intended aggression by a capable entity to harm any aspect or all of a facility or its contents.  THREAT can also be considered as any potential event or act, deliberate or accidental, that could cause injury to employees or assets.

THREAT AND RISK ASSESSMENT i.e., an evaluation of the vulnerability of a facility or asset which is generally provided as a report prior to designing a security solution.

TIME TO REPAIR is the time measured from informing the maintenance provider of a problem to the correction and the return to full service of the defective system.

TOGGLE generally refers to the ability to activate a control function repeatedly thereby changing the output state between 2 alternative conditions.  This may be the control of lights, i.e., turning them on and then off, or the control of a door, i.e., latching a door open and closed.  Such toggling may, for example, be activated by activating a button or by using a specially programmed access card

TROUBLE INPUTS are internal inputs defined within a security system which generate “alerts” to notify the system operators of an internal fault or “trouble”.  Such “troubles” need attention even if the reported problem does not appear to be causing any immediate concerns.  Typical trouble inputs may include battery failure, AC power failure, power supply failure, LAN communications failure, phone line failure excess temperatures in the cabinet, system restart etc.

UNDERWRITERS LABORATORIES or UNDERWRITERS LABORATORIES OF CANADA is one of a number of global industry-based safety testing and certification laboratories which has been approved to perform tests of equipment where otherwise CSA testing would be required.

UNINTERRUPTIBLE POWER SUPPLY is an alternative source of main electrical power which is always available in the event that the primary source of power fails.  Generally, the UPS power is on line at all times thereby ensuring that the power to the equipment never fails for even an instant.  In many circumstances the UPS is associated with a Standby Generator which stars up and can generate power for a long time after about 1 minute thereby providing power for a long time if the Utility power is absent.

VLAN  “virtual LAN” is any broadcast domain that is partitioned and isolated in a computer network at the data link layer (OSI layer 2).  LAN is local area network and in this context virtual refers to a physical object recreated and altered by additional logic.  VLANs work by applying tags to network frames and handling these tags in networking systems thereby creating the appearance and functionality of network traffic that is physically on a single network but acts as if it is split between separate networks.

VULNERABILITY - an inadequacy related to security that could permit a threat to cause injury.

WALK TEST is a method for testing sensors, generally in an operational security system, without causing false, system alarms.  During a walk test, a person will go through each area and intentionally activate sensors so that they are recognized by the system.  Arguably, the most important sensors to check during a Walk Test are motion sensors.  This is because motion sensors are particularly prone to false alarms when they are mounted improperly.  However, the testing process should also include all other sensors which are being monitored.  During the Walk Test, the faulted zones will be displayed, but no alarms will be reported to the central station.

WARRANTY is the requirement for the contractor to provide a reliable system with an acceptable “return to service” response time.  Typically, this requirement will define availability of parts and trained technicians for a specified period.

WHMIS The Workplace Hazardous Materials Information System are laws, created in 1988 to: give employers and workers information about the hazardous products or chemicals they may be exposed to at work.  By international agreement this is now synonymous with a global system known as the Globally Harmonized System for the Classification and Labelling of Chemicals (GHS).

WIDE AREA NETWORK is a computer network spanning regions, countries, or even the world and which may be partially made of infrastructure belonging to many and possibly unknown partners.  The application is generally to provide for sharing of data or for the networking of computers.

Wi-Fi is a family of wireless network protocols, based on the IEEE 802.11 family of standards, which are commonly used for   area networking of devices and Internet access.  Wi-Fi is a trademark of the non-profit Wi-Fi Alliance which restricts the use of the term Wi-Fi Certified to products that successfully complete interoperability certification testing.  Communication using Wi-Fi allows for wireless local area networking (See Appendix D, Standards Applicable to Regional Security Projects, for details of 802.11)

ZONES defines a series of clearly discernible and securable spaces to progressively control access.

  - Appendix D – Standards Applicable to Regional Security Projects

This appendix lists the Standards which are generally applicable to portions of the security work specified by the York Region for Security related work.  It is the contractor’s responsibility to ensure that the most recent version of such Standards or Codes is being used.  Should there be any conflicts which arise in the interpretation of such documents the Region of York shall be the final authority.

Standards are divided into distinct groupings and when enforced by Regulation or by Legal Statutes are generally referred to as Codes:

- Internal, i.e., York Region policy and experience-based policies

- Municipal, Provincial and National Standards

- Technology Standards

Any specific standards will be referenced for particular projects as required.  Standards shall always be the most current commonly available version at the time the contract was awarded.  This list is not intended to be exhaustive but is intended to guide contractors.  Contractors are always responsible for adhering to all required and customary standards, best practices and are exclusively responsible for obtaining clarification if required.  The primary authoring agencies of the Codes which may be encountered are identified below.  It must be noted that these agencies are not necessarily respected or approved in Canadian jurisdictions and the list is not necessarily complete.:

| ANSI |  | American National Standards Association, |
| --- | --- | --- |
| BICSI |  | Building Industry Consulting Service International |
| CCIR |  | Consultative Committee for International Radio |
| CE |  | Conformity for Europe |
| CSA |  | Canadian Standards Association |
| EEMAC |  | Electrical Equipment Manufacturers Association of Canada |
| EIA |  | Electronic Industry Association |
| ETL |  | Electrical Testing Laboratories |
| FCC |  | Federal Communications Commission |
| IEEE |  | Institute of Electrical and Electronic Engineers |
| ISO |  | International Organization for Standardization |
| JPEG |  | Joint Photographic Experts Group |
| MPEG |  | Moving Picture Experts Group |
| NFPA |  | National Fire Prevention Association |
| NRC |  | National Research Council (of Canada) |
| NTSC |  | National Television Systems Committee |
| PAL |  | Phase Alternating by Line |
| TIA |  | Telecommunications Industry Association, 568, 569, 606, 607 etc |
| UL |  | Underwriters Laboratories Inc. |
| ULC |  | Underwriter’s Laboratories of Canada |

The following Codes may be applicable to most projects

CEC					Canadian Electrical Code 2018, Part 1, C22.1-18

OESC					Ontario Electrical Safety Code 2018

OBC					Ontario Building Code 2012 updated 2020

NBC					National Building Code 2015

NFPA					National Fire Prevention Association 70E, 101, 2021

ULC					Underwriter’s Laboratories of Canada, 437 etc

TIA					Telecommunications Industry Association, 568, 569, 606, 607 etc

EEMAC 				TC3 PVC Fittings for use with Rigid PVC Conduit and Tubing.

CSA C22.2 No. 211.2-06 Rigid PVC (Unplasticized) Conduit.

CAN/CSA C22.2 No. 18-06, Outlet Boxes, Conduit Boxes, and Fittings and Associated Hardware.

Canadian ICES-003 (Interference Causing Equipment Standard Policy)

ANSI / TIA-606-C Cable Labelling Standards (July 2017)

TIA-568.0-D Generic Telecommunications Cabling for Customer Premises

TIA-568.1-D Commercial Building Telecommunications Cabling Standard

TIA-568.2-D Balanced Twisted-Pair Telecommunications Cabling and Components Standard

TIA-568.3-D Optical Fibre Cabling Components

TIA-569-D Telecommunications Pathways and Spaces

TIA-606-C Administration Standard for Telecommunications Infrastructure

TIA-607-C Generic Telecommunications Bonding and Grounding (Earthing) for Customer Premises

TIA-862-B Building Automation Systems Cabling Standard

TIA-942-B Telecommunications Infrastructure Standard for Data Centers

TIA-1005-A Telecommunications Infrastructure Standard for Industrial Premises

TIA-1179-A Healthcare Facility Telecommunications Infrastructure Standard

ISO/IEC 11801 Generic Cabling for Customer Premises

IEEE 802.3 Standards

IEEE 802.3af Power over Ethernet (PoE) Standard

IEEE 802.3at Power over Ethernet+ (Plus) Standard

IEEE 802.3bt 4-Pair Power Over Ethernet (4PPoE) Standard

IEEE 802.3an Physical Layer and Management Parameters for 10 Gbps Operation Type 10GBASE-T

IEEE 802.3ba Media Access Control Parameters, Physical Layers and Management Parameters for 40 Gbps and 100 Gbps Operation

IEEE 802.11 Wireless Standard

IEEE 802.11 STANDARDS Wireless Standard

IEEE 802.11, the Wi-Fi standard, denotes a set of wireless LAN/WLAN standards developed by Working Group 11 of the IEEE LAN/MAN standards committee (IEEE 802).  The term 802.11x is also used to denote this set of standards and is not to be mistaken for any one of its elements.  There is no single 802.11x standard.

IEEE 802.11 details a wireless interface between devices to manage packet traffic (to avoid collisions, etc.).  Some common specifications and their distinctive attributes include the following:

IEEE 802.11a – Operates in the 5 GHz frequency range (5.125 to 5.85 GHz) with a maximum 54 Mbps signalling rate.  The 5 GHz frequency band isn’t as crowded as the 2.4 GHz frequency because it offers significantly more radio channels than the 802.11b and is used by fewer applications.  It has a shorter range than 802.11g, is actually newer than 802.11b and is not compatible with 802.11b.

IEEE 802.11b – Operates in the 2.4 GHz Industrial, Scientific and Medical (ISM) band (2.4 to 2.4835 GHz) and provides signalling rates of up to 11 Mbps.  This is a commonly used frequency.  Microwave ovens, cordless phones, medical and scientific equipment, as well as Bluetooth devices, all work within the 2.4 GHz ISM band.

IEEE 802.11e – Ratified by the IEEE in late September 2005, the 802.11e quality-of-service specification is designed to guarantee the quality of voice and video traffic.  It is particularly important for companies interested in using Wi-Fi phones.

IEEE 802.11g – Similar to 802.11b, this standard supports signalling rates of up to 54 Mbps.  It also operates in the heavily used 2.4 GHz ISM band but uses a different radio technology to boost overall throughput.  Compatible with older 802.11b.

IEEE 802.11i – Also sometimes called Wi-Fi Protected Access 2 (WPA 2), 802.11i was ratified in June 2004.  WPA 2 supports the 128-bit-and-above Advanced Encryption Standard, along with 802.1x authentication and key management features.

IEEE 802.11k – Passed in June 2008, the 802.11k Radio Resource Management Standard will provide measurement information for access points and switches to make wireless LANs run more efficiently.  It may, for example, better distribute traffic loads across access points or allow dynamic adjustments of transmission power to minimize interference.

IEEE 802.11n – Ratified in September 2009, 802.11n is a set of standards for wireless local area network (WLAN) communications, developed by the IEEE LAN/WAN Standards Committee (IEEE 802) in the 5 GHz and 2.4 GHz public spectrum bands.  The proposed amendment improves upon the previous 802.11 standards by adding multiple-input multiple-output (MIMO) and many other newer features.

IEEE 802.11ac – Published in January 2014 by the IEEE 802.11 LAN/WAN Standards Committee, the standard increases WLAN multi-station throughput from the previous 802.11n standard to at least 1 gigabit per second and to a single link throughput of at least 500 megabits per second (500 Mbit/s).  The increased throughput is achieved by utilizing wider RF bandwidth (up to 160 MHz), more MIMO spatial streams (up to eight), downlink multi-user MIMO (up to four clients), and high-density modulation (up to 256-QAM).

IEEE 802.11ad – This amendment defines modifications to both the IEEE 802.11 physical layers (PHYs) and the IEEE 802.11 medium access control layer (MAC) to enable operation in frequencies around 60 GHz and capable of very high throughput up to 7 Gbps.

For further information on cabling standards, please obtain the full versions of the original standards documents.

TIA-568.0-D (2009) 	Generic Telecommunications Cabling for Customer Premises

TIA-568.1-D (2009) 	Commercial Building Telecommunications Cabling Standard

TIA-568.2-D 2009)		Balanced Twisted-Pair Telecommunications Cabling and Components Standard

TIA-568.3-D (2009)	Optical Fibre Cabling Components

TIA-569-D (2015) 		Telecommunications Pathways and Spaces

TIA-606-C (2012) 		Administration Standard for Telecommunications Infrastructure

TIA-607-C (2015) 	Generic Telecommunications Bonding and Grounding (Earthing) for Customer Premises

TIA-862-B (2011) 		Building Automation Systems Cabling Standard

TIA-942-B (2012) 		Telecommunications Infrastructure Standard for Data Centres

TIA-1005-A (2012) 	Telecommunications Infrastructure Standard for Industrial Premises

TIA-1179-A (2010) 	Healthcare Facility Telecommunications Infrastructure Standard

IS0/IEC 11801 (2002) 	Generic Cabling for Customer Premises

IEEE 802.3af (2003) 	Power over Ethernet (PoE) Standard

IEEE 802.3at (2009)	 Power over Ethernet+ (Plus)

IEEE 802.3an (2006) 	Physical Layer and Management Parameters for 10 Gbps Operation Type 10GBASE-T

IEEE 802.3ba (2010) 	Media Access Control Parameters, Physical Layers and Management Parameters for 40 Gbps and 100 Gbps Operation

IEEE 802.3bm (2015) 	Physical Layer specifications and management parameters for 40 Gbps operation over single-mode fibre (40GBASE-ER4) and for 100 Gbps operation over multimode fibre (100GBASE-SR4)

IEEE 802.3bq (2016) 	Physical Coding Sublayer (PCS) interfaces and new Physical Medium Attachment (PMA) sublayer interfaces for 25 Gbps Ethernet and 40 Gbps Ethernet

IEEE 802.3bz (2016) 	Physical Layer specifications, and management objects for the transfer of Ethernet format frames at 2.5 Gbps and 5 Gbps over balanced twisted-pair transmission media

IEEE 802.3bs (2017) 	Physical Layer specifications, and management parameters for the transfer of IEEE 802.3 format frames at 200 Gbps and 400 Gbps.

IEEE 802.3bt (2018)	Physical Layer and Management Parameters for Power over Ethernet over 4 pairs

IEEE 802.11 Wireless Standard

802.11ac (2014)

802.11n (2009)

802.11k (2008)

802.11e (2005)

802.11i (2004)

802.11a (2003)

802.11b (2003)

802.11ac (2014)

802.11ad (2012)

802.11g (2003)

Documentation submissions

All documents are to be submitted to York Region using:

- Microsoft Office 2019 or later as appropriate

- AutoCAD 2019 or later as appropriate

- Photographs shall be formatted in JPG but shall be no larger than 10 MB each.

Unless otherwise agreed to or documented in the Contract Documents, hardcopy submittals shall:

- Be printed single side, 8.5 x 11 inches and bound;

- The binding system which is used shall be sufficiently durable for the purpose, i.e., for review or for ongoing reference.  Typical binding systems are 3 rings binders, Cerlox and Wire Binding Spines.  Note that only the 3 rings binder can be easily updated;

- Pages shall be numbered in the format of “page 23 of 120”, i.e., indicating the total number of pages in the document; and

- Where colour is used to explain any aspect of the documentation the submittal must be printed in colour.

Unless otherwise agreed to or documented in the Contract Documents, Digital submittals shall:

- Be provided in both Adobe’s Portable Document Format (PDF) and in the source document editing format, e.g., Microsoft Word etc.  using software and versions which comply with the Region’s Standards as defined in this Appendix;

- The submittal of the digital information my be provided on a portable media, e.g., a thumb drive or a Digital Video Disk (DVD), or through an e-mail or File Transfer Protocol (FTP) exchange;

- Be certified by the sender to be free of all forms of malware, including trojan horses, viruses, worms etc;

- Be free of any encryption, locks, passwords or devices to restrict access unless this is acknowledged and documented prior to the document transmission; and

- Not be subject to any form of proprietary restrictions or copyright.

  - Appendix E – Standardised Security Configurations

This section provides typical assemblies, components, drawing conventions and title blocks as used by York Region and which shall be used as the basis of all security contracts undertaken for York Region.  If there is a requirement for a function which are not addressed by any of the supplied assemblies, the Contractor shall inform the York Region Project Manager and obtain suitable guidance.

The Contractor shall obtain the most up to date version of these diagrams from the Region prior to preparing the drawings so as to ensure that any updates or technology changes have been incorporated.

  - Appendix F – Procedure for Equipment Substitution

- INTRODUCTION

The following procedures and forms are provided to the Contractor in order to ensure that if the pre-approved equipment is not going to be installed, there is a clear and fair process to be followed by all parties.  The procedure and form require that the costs, quality, reliability as well as potential implications have all been identified and considered.

- SUBSTITUTION PROCEDURES

PART 1	GENERAL

.2.1.1	Definitions

Substitutions:  Changes in products, materials, equipment, and methods of construction from those required by the Contract Documents and proposed by Contractor.

Architect:  Reference to Architect in this Appendix is a reference to the authorised person overseeing the construction contract who may be an Architect, Engineer, Project Manager or a Consultant.

- Substitutions for Cause:  Changes proposed by Contractor that are required due to changed Project conditions, such as unavailability of product, regulatory changes, or unavailability of required warranty terms.

- Substitutions for Convenience:  Changes proposed by Contractor or Owner that are not required in order to meet other Project requirements but may offer advantage to Owner.

2.1.2	Submittals

Substitution Requests:  Prepare and submit each substitution request for consideration using the procedures listed in Section “Submittal Procedures”.  Identify product or fabrication or installation method to be replaced.  Include Specification Section number and title and Drawing numbers and titles.

  - Substitution Request Form:  Use copy of form provided in this Appendix.

  - Documentation:  Show compliance with requirements for substitutions and the following, as applicable:

    - Statement indicating why specified product or fabrication or installation cannot be provided, if applicable.

    - Coordination information, including a list of changes or modifications needed to other parts of the Work and to construction performed by Owner and separate Contractors, that will be necessary to accommodate proposed substitution.

    - Detailed comparison of significant qualities of proposed substitution with those of the Work specified.  Include annotated copy of applicable specification section.  Significant qualities may include attributes such as performance, weight, size, durability, visual effect, sustainable design characteristics, warranties, and specific features and requirements indicated.  Indicate deviations, if any, from the Work specified.

    - Product Data, including drawings and descriptions of products and fabrication and installation procedures.

    - Samples, where applicable or requested.

    - Certificates and qualification data, where applicable or requested.

    - List of similar installations for completed projects with project names and addresses and names and addresses of architects and owners.

    - Material test reports from a qualified testing agency indicating and interpreting test results for compliance with requirements indicated.

    - Research reports evidencing compliance with building code in effect for Project, from ICC-ES.

    - Detailed comparison of Contractor's construction schedule using proposed substitution with products specified for the Work, including effect on the overall Contract Time.  If specified product or method of construction cannot be provided within the Contract Time, include letter from manufacturer, on manufacturer's letterhead, stating date of receipt of purchase order, lack of availability, or delays in delivery.

    - Cost information, including a proposal of change, if any, in the Contract Sum.

    - Contractor's certification that proposed substitution complies with requirements in the Contract Documents except as indicated in substitution request, is compatible with related materials, and is appropriate for applications indicated.

    - Contractor's waiver of rights to additional payment or time that may subsequently become necessary because of failure of proposed substitution to produce indicated results.

  - Architect's Action:  If necessary, Architect will request additional information or documentation for evaluation within seven days of receipt of a request for substitution.  Architect will notify Contractor of acceptance or rejection of proposed substitution within 10 days of receipt of request, or seven days of receipt of additional information or documentation, whichever is later.

- Forms of Acceptance:  Change Order, Construction Change Directive, or Architect's Supplemental Instructions for minor changes in the Work.

- Use product specified if Architect does not issue a decision on use of a proposed substitution within time allocated.

- The architect shall identify costs which may be associated with the revisions to the Contract documents or Contract Drawings and identify who shall be responsible for paying such costs.

2.1.3	Quality Assurance

- Compatibility of Substitutions:  Investigate and document compatibility of proposed substitution with related products and materials.  Engage qualified testing agency to perform compatibility tests recommended by manufacturers.

2.1.4	Procedures

- Coordination:  Modify or adjust affected work as necessary to integrate work of the approved substitutions.

PART 2	 PRODUCTS

3.1.1	Substitutions

Substitutions for Cause:  Submit requests for substitution immediately upon discovery of need for change, but not later than 15 days prior to time required for preparation and review of related submittals.

Conditions:  Architect will consider Contractor's request for substitution when the following conditions are satisfied.  If the following conditions are not satisfied, Architect will return requests without action, except to record noncompliance with these requirements:

- Requested substitution is consistent with the Contract Documents and will produce indicated results.

- Substitution request is fully documented and properly submitted.

- Requested substitution will not adversely affect Contractor's construction schedule.

- Requested substitution has received necessary approvals of authorities having jurisdiction.

- Requested substitution is compatible with other portions of the Work.

- Requested substitution has been coordinated with other portions of the Work.

- Requested substitution provides specified warranty.

- If requested substitution involves more than one contractor, requested substitution has been coordinated with other portions of the Work, is uniform and consistent, is compatible with other products, and is acceptable to all contractors involved.

Substitutions for Convenience:  Architect will consider requests for substitution if received within 60 days after commencement of the Work.  Requests received after that time may be considered or rejected at discretion of Architect.

Conditions:  Architect will consider Contractor's request for substitution when the following conditions are satisfied.  If the following conditions are not satisfied, Architect will return requests without action, except to record noncompliance with these requirements:

- Requested substitution offers Owner a substantial advantage in cost, time, energy conservation, or other considerations, after deducting additional responsibilities Owner must assume.  Owner's additional responsibilities may include compensation to Architect for redesign and evaluation services, increased cost of other construction by Owner, and similar considerations.

- Requested substitution does not require extensive revisions to the Contract Documents.

- Requested substitution is consistent with the Contract Documents and will produce indicated results.

- Substitution request is fully documented and properly submitted.

- Requested substitution will not adversely affect Contractor's construction schedule.

- Requested substitution has received necessary approvals of authorities having jurisdiction.

- Requested substitution is compatible with other portions of the Work.

- Requested substitution has been coordinated with other portions of the Work.

- Requested substitution provides specified warranty.

- If requested substitution involves more than one contractor, requested substitution has been coordinated with other portions of the Work, is uniform and consistent, is compatible with other products, and is acceptable to all contractors involved.

  - Appendix G – Standardised Abbreviations

The following abbreviations are provided for the convenience of the reader.  Note that some of the abbreviations are case sensitive and may be used in conjunction with other units.

A	Amps (Amperes)

AC	Access Control

AC 	Alternating Current (see DC)

ACS	Access Control System

ADO	Automatic Door Operator

ADSL	Asymmetric Digital Subscriber Line

AM	Amplitude Modulation (as in broadcast radio)

ANSI	American National Standards Institute

API	Application Programming Interface

ASCII	American Standard Code for Information Interchange

ASHRAE	American Society of Heating, Refrigeration and Air-Conditioning Engineers

ATM	Asynchronous Transfer Mode

A to D	Analog to Digital conversion

b	bit (digital bit)

B	Byte

BCP	Business Continuity Plan

BICSI	Building Industry Consulting Service International

BIT	Burn-In Testing

BMP	Best Maintenance Practices

BSA	Business System Analyst)

bps	bits per second

C	Celsius, Degrees

C	Common (as in electrical connection)

C and D	Collection and Distribution

CA	Contract Administrator

CAC	Common Access Card

CBRN	Chemical, Biological, Radiological and Nuclear (as in threat)

CBRNE	Chemical, Biological, Radiological, Nuclear and Explosive (as in threat)

CCIR	Consultative Committee for International Radio

CCTV 	Closed Circuit Television

CCVE	Closed Circuit Video Equipment

CE	Conformity for Europe (as in European Common Market)

CEC	Canadian Electrical Code

cm	Centimetre

CMMI	Capability Maturity Model Integration

CMP	Plenum Rated Cable

CMR	Riser Rated Cable

CPU	Central Processing Unit

CPTED	Crime Prevention Through Environmental Design

CSA	Canadian Standards Association

CSV 	Comma Separated Values (Comma Separated Variables)

dB	decibels (logarithmic ratio of sound levels, usually relative to 1 mW)

DC	Direct Current (see AC)

DIN	Deutsche Institut für Normung i.e., German Institute for Standardisation

DSL	Digital Subscriber Line

DTMF	Dual Tone Multi-Frequency

D to A	Digital to Analog Conversion

DVMS	Digital Video Management System

DVR	Digital Video Recorder, a precursor to the NVR

EC	Environment Canada

EEMAC	Electrical Equipment Manufacturers Association of Canada

EIA	Electronic Industry Association

EN	European Standards (European Norms)

ENV	Environmental Department (York Region)

EOL	End of Line (Supervision Resistor)

ESA	Electrical Safety Authority (Ontario)

ETL	Electrical Testing Laboratories

F	Fahrenheit, Degrees

F	Farad, the unit of Capacitance

FAR	False Alarm Ratio

FAR	False Alarm Rate

FCC	Federal Communications Commission (US Government Agency)

FDDI	Fibre Distributed Data Interface

FIPPA	The Freedom of Information and Protection of Privacy Act provides individuals with a right of access to certain records and personal information under the custody or control of institutions covered by the Act.

FM	Frequency Modulation (as in broadcast radio)

FM	Facility Management

fps	frames per second, number of individual still images recorded or shown per second.

ft	Foot or Feet

FT-4	Flame Test Level 4 (Riser Rated Cable)

FT-6	Flame Test Level 6 (Plenum Rated Cable)

G	Abbreviation for Giga, see Giga

GFCI	Ground Fault Circuit Interrupter (see GFI)

GFI	Ground Fault Interrupter (see GFCI)

Giga	The prefix to a value meaning 1,000 000 000 or 109

HTML	Hyper Text Mark-up Language

H	Henry, the unit of inductance

Hz	Hertz (frequency in cycles/second)

IDS	Intrusion Detection System

IEC	International Electrotechnical Commission

IEEE	Institute of Electrical and Electronics Engineers (A standards organisation)

in or ins	Inch or Inches

IP	Internet Protocol, also Intellectual Property

IR	Infra-Red

IS	Intrinsically Safe

ISC	Intelligent System Controller

ISO	International Organization for Standardization

ISP 	Internet Service Provider

IT 	Information Technology

ITS	Information Technology Services

ITU	International Telecommunication Union (A UN Agency)

ITU-T	ITU Telecommunication Standardisation Sector

JPEG	Joint Photographic Experts Group

k	kilo (as in 1,000 of subsequent unit)

K	Kelvin, Degrees

LAN	Local Area Network

LPR	Licence Plate Recognition

LTE	Long Term Evolution

m	Metre

m	milli (as in 0.001 of subsequent unit)

M	Mega (as in 1,000,000 of subsequent unit)

MFIPPA	The Municipal Freedom of Information and Protection of Privacy Act provides individuals with a right of access to certain records and personal information under the custody or control of institutions covered by the Act.

micro 	a value of 0.000 001 or a millionth of the subsequent unit (µ)

mm	millimetre

MPEG	Moving Picture Experts Group

MSDS	Material Safety Data Sheet (see SDS)

MTBF	Mean Time Between Failures

MTTF	Mean Time to Failure

MTTR	Mean Time To Repair

nano 	a value of 0.000 000.001 or 10-9

NBC	National Building Code (of Canada)

NC	Normally Closed

NEC	National Electrical Code (US Electrical Code)

NEMA	National Electrical Manufacturers Association

NFPA	National Fire Prevention Association

NO	Normally Open

NPT	National Pipe Thread

NTSC	National Television Systems Committee (also form of TV encoding)

NVR	Network Video Recorder

O&M	Operations and Maintenance

OBC	Ontario Building Code

ODBC	Open Database Connectivity

OEM	Original Equipment Manufacturer

OESC	Ontario Electrical Safety Code

OHSA	Occupational Health and Safety Act (Ontario)

OHSS	Ontario Health and Safety Standards

OMM	Operations Maintenance Monitoring (York Region)

OSI	Open Systems Interconnection (model)

p	pico, the prefix to any unit to indicate 10-12, i.e., 0.000 000 000 001

Pa	Pascal (Unit of Pressure - see PSI)

PAL	Phase Alternating by Line (form of TV encoding)

PDC 	Power Distribution Centre

PIT	Pre-Installation Testing

PPI	Pixels per Inch

PPM	Preventive Maintenance (same as Preventative)

PMPP	Point to Multipoint Protocol

POD	Probability Of Detection

POE		Power Over Ethernet

POP	Proof Of Performance Testing

PPP 	Point-to-Point Protocol

PSAR	Physical Security Assessment Report

PSI	Pounds per Square Inch (see Pascal)

PTZ	Pan, Tilt and Zoom (3 axes of motion for a surveillance camera)

QC / QA 	Quality Control / Quality Assurance

QAM	Quadrature Amplitude Modulation (as in digital TV)

RAID	"Redundant Array of Inexpensive Disks" or "Redundant Array of Independent Disks" is a data storage virtualization technology that combines multiple physical disk drive components into one or more logical units for the purposes of data redundancy, performance improvement, or both.

RH	Relative Humidity, expressed as a percentage, indicates a present state of absolute humidity relative to a maximum humidity given the same temperature.

RTD	Resistive Temperature Detector

RU	Rack Unit, also abbreviated as “U”.

SAE	Society of Automotive Engineers

SCADA	Supervisory Control And Data Acquisition

SDS	Safety Data Sheet (formerly MSDS)

SDK	Software Development Kit

SI	International System of Units (Metric system)

SIL	Safety Integrity Level, 1, 2, 3 or 4 (IEC 61508)

SIT	System Integration Test

SMTP 	Simple Mail Transfer Protocol

SPICE	Software Process Improvement and Capability dEtermination

SQL 	Structured Query Language

T	Temperature

T	Abbreviation for Tera (see Tera)

TCP/IP	Transmission Control Protocol (TCP) / Internet Protocol (IP)

Tera	is the prefix to indicate 1012

TIA	Telecommunications Industry Association (standards agency)

TRA	Threat and Risk Assessment

TSSA	Technical Standards and Safety Authority.  The Technical Standards and Safety Authority (TSSA) promotes and enforces public safety in Ontario.

TTR	Time To Repair

U	Rack Unit also abbreviated as “RU”.

UL	Underwriters Laboratories (USA)

ULC 	Underwriters Laboratories of Canada

UPS	Uninterruptible Power Supply

UTP	Unshielded Twisted Pair, generally referring to Cat 4, Cat 5 or Cat 6 cables

UV	Ultra Violet

V	Volt

VAR	Value Added Reseller

VMS	Video Management System

WAN 	Wide Area Network

WHMIS	Workplace Hazardous Materials Information System

  - Appendix H – Environmental Requirements

The following requirements are identified for all Security equipment provided to York Region unless otherwise identified.

Unless specifically identified all indoor and outdoor equipment should be capable of performing and or surviving the following operational conditions.  Note that particularly in moist or wet locations the contractor has the responsibility to minimise or eliminate all electro chemical potentials which are a primary cause of corrosion.  These specifications are intended to address only the requirements in “normal” spaces and do not extend to the special requirements which may exist in “special” locations, such as sewage or water treatment facilities.

Outdoor Operational Environments

Air Temperature Minimum:		-40 °C (-40 °F)

Air Temperature Maximum		+40 °C (105 °F)

Ambient Humidity			10% to 80% (RH)

Wind					240 km/hr (150 mph)

Rain / Snow 				6 mm/min

Solar Radiation				1000 W/m2

Vibration					1.5 mm displacement,

20 m/s2 acceleration,

2 – 200 Hz frequency)

Dust					3.0 mg / m2h

Indoor Operational Environments

Air Temperature Minimum:		10 °C (50 °F)

Air Temperature Maximum		35 °C (95 °F)

Ambient Humidity			10% to 80% (RH)

Vibration					1.5 mm displacement,

20 m/s2 acceleration,

2 – 200 Hz frequency)

Storage Environments

Air Temperature Minimum:		-45 °C (-50 °F)

Air Temperature Maximum		45 °C (115 °F)

Ambient Humidity			10% to 90% (RH)

  - Appendix I – Access Control System Value Added Resellers

.1	Security Systems shall be provided by one of the VARs prequalified under Request for Pre-qualification No. PQ-19-214 listed below.  The Contractor shall ensure that the VAR provides the services as detailed in the Contract Documents:

.1.1 	The following are the pre-qualified Lenel Security System Value Added Resellers (as of December 2020):

Chubb, UTC Fire and Security Canada Inc.

Stephen Yates

stephen.yates@chubbedwards.com

(416) 659-1754

Extravision Security Technologies Inc.

Andrew Reedman

andrew.reedman@extravision.ca

(416) 704-7434

Paladin Technologies Inc.

Marc Kingsbury

mkingsbury@paladintechnologies.com

(647) 459-5691

Securitas Electronic Security (Canada) Inc.

Tom Nanou

Tom.nanou@securitasES.com

(416) 678-7353

.2	Installation and integration of the Lenel security system(s) shall be completed by one of the Lenel System Installers pre-qualified under Request for Pre-qualification No. PQ-19-215 listed below.

.3	The following are the pre-qualified Lenel Security System Installers (alphabetical order)

Electro-Works Ltd.

Dondi Keough

dondi@tcsecure.ca

Phone: (416) 529-7180

OZZ Electric Inc.

Steve Trabona

strabona@ozzelectric.com

Phone: (905) 695-2912

Plan Group Inc.

Mike Van Steendelaar

mvansteendelaar@plan-group.com

Phone (416) 635-9040

  - Appendix J – List of Approved Security Equipment

The following equipment is pre-approved and detailed equipment submission is not required.  Note, however that the contractor is responsible to ensure that the version of equipment must be fully compatible with the environment currently in use or envisaged for imminent use at the York Region.  Note that in those categories where multiple manufacturers and models are identified, the contractor is responsible to identify to York Region, the model and manufacturer which is to be used for any given project.

If the contractor requires to use equipment not shown in this listing, full details and justification shall be provided in accordance with the procedure set out in Appendix F “Procedure for Equipment Substitution”.  The York Region has the authority to accept or to reject the use of the proposed substitute equipment.

If the function to be provided by the “proposed equipment” is addressed by any equipment which is not listed, then the proposed equipment must be processed through a “Procedure for Equipment Substitution” as documented in Appendix F.

Some of the door contacts used by York Region need to comply with the requirements of Hazardous Locations and therefore shall be certified for use in such areas (Explosion Proof).  Even for use in such areas, an approach referred to as “Intrinsically Safe” may be used.  This approach requires the use of a certified “barrier” which ensures very low current levels when used with devices which themselves comply with the requirements of a “simple apparatus” and do not need certification.  For example, when using a SIL rated barrier, regular door contacts (not explosion proof) may be acceptable for use in a hazardous location.  This document is not the place to undertake a detailed design or to recommend solutions.  The list of approved equipment which follows includes alternative devices which may be considered for Hazardous Locations.

The information for the principal equipment is listed in Appendices K, L, M, N, O, P and Q and is summarised in the tables below.

- Access Control Components

| Part# | Description |
| --- | --- |
| LNL-2220 | Intelligent Dual Reader Controller |
| LNL-3300 | Intelligent System Controller |
| LNL-4420 | Advanced Dual Reader Controller |
| LNL-1300 | Single Reader Interface Module |
| LNL-1320 | Dual Reader Interface Module |
| LNL-1100 | Input Control Module |
| LNL-1200 | Output Control Module |
| RP15/RP40/RPK40 | HID Corporation, multiCLASS SE technology card reader to suit application |
| SD-72, … SD-84 | Magnetic Door Contact by Tane Alarm |
| 184-12, 194-12 | Magnetic Door Contact by George Risk Industries (GRI) |
| MET-44 WG | Overhead Door Contact by Tane Alarm |
| 4532D-36 | Overhead Door Contract by George Risk Industries (GRI) |
| LSX Series Micro Switches | Explosion Proof Mechanical Door Contact by Honeywell |
| TA-4106-ES | Magnetic Door Contact, Manufacturer unknown; available from K M Thomas |
| EA800, EA880 | Explosion Proof Limit Switches by NAMCO, Available from Galco |
| HSS-L25-800, HSS-L1.5-101 | Simple Apparatus Contacts in an Intrinsically Safe Scheme, by Magnasphere |
| D5030 I.S. SIL3 | Relay Out Repeater by GMInternational, available from Exloc Instruments |
| IS310/IS320 | Request-to-Exit (RTE) motion sensors |
| 2966906 Phoenix | SPST Relay 12VDC with base DIN rail-mount or equivalent |
| 2900329 Phoenix | DPDT Relay 12VDC with base DIN rail-mount or equivalent |
| IM‐1270 | 12V/7Ah Backup Battery |
| LSP MCLASS FlexPower power supplies and power distribution components | Life Safety Power MCLASS FlexPower Power Supply, Enclosure, Door with backplane/standoffs, no wire management. |
| Hoffman NEMA 2 Enclosure | Hoffman Concept Series enclosure to suit application and to fit corresponding LSP Enclosure. Shall be lockable with Medeco CLIQ Systems or AWP Padlock and to work with the Region owned Medeco Electronic Keys. |
| Hoffman NEMA 3 Enclosure | Hoffman Concept Series enclosure to suit application and to fit corresponding LSP Enclosure. Shall be lockable with Medeco CLIQ Systems or AWP Padlock and to work with the Region owned Medeco Electronic Keys. |
| Hoffman NEMA 4 Enclosure | Hoffman Concept Series enclosure to suit application and to fit corresponding LSP Enclosure. Shall be lockable with Medeco CLIQ Systems or AWP Padlock and to work with the Region owned Medeco Electronic Keys. |
| Hoffman Enclosure Accessories | Hoffman Enclosures shall be completed with ADP2, CWHPTO padlock handle, LED24V15 LED Enclosure Light, and full-conductive back panel or equivalent. |
| R991RBPTD9 | Pneumatic delay arming Button, w/delay RED Blank by RCI (Dormakaba) |
| HES 1006 KD | HES 1006 KD 630 Electric Strike (provided by Locksmith) |
| HES 9600 | HES 9600 The surface mounted, windstorm rated solution for rim exit devices (Provided by Locksmith) |
| Smart Pac III | In-Line Power Controller for electric strikes by HES (Assa-Abloy) |
| 1N 4007 | Snubbing (Snubber) Diodes (any manufacturer) |

- Intrusion Detection System Components

| Part# | Description |
| --- | --- |
| B9512G | Bosch D9512G Control Panel Alarm Panel |
| B208 SDI2 | Bosch B208 SDI2 8-Input Expansion Module |
| B308 SDI2 | Bosch B308 SDI2 8-Output Expansion Module |
| B942 | Bosch B942 Touch Screen Keypad |
| B930 ATM | Bosch B930 ATM Style-Alpha Numeric Keypad (SD12) |
| B56 | B56 Keypad Surface Mount Box |
| B426 | Bosch B426 Conettix Ethernet Communication Module |
| B443 | Bosch Plug-in Cellular, HSPA+ (3G+) |
| B440 | Bosch Plug-in Cellular module |
| FG-1625F or equivalent | Glass Break Detector |
| DS940Q, Optex DX40 or equivalent | Motion Detector |

  - Appendix K – Approved Access Control Equipment

- Control Panel

Lenel Intelligent System Controllers (To be specified by the Contractor during the design of the security system).

- LNL-2220 Intelligent Dual Reader Controller (IDRC) provides a single board solution for interfacing one or two doors to an OnGuard® system.  On-board Ethernet 10/100Base-T port, 6 MB on-board, non-volatile flash memory, Battery-backed, non-volatile storage of 50,000 events, 16 different formats, 12 or 24 VDC input power, 32 downstream devices.

- The LNL-3300 Intelligent System Controller (ISC) by Lenel is designed for advanced access control applications.  On-board Ethernet 10/100Base-T port, 15 MB on-board, non-volatile flash memory, Battery-backed, non-volatile storage of 50,000 events, 16 different formats, 12 or 24 VDC input power, 64 downstream devices via two individual downstream RS-485 ports.

- The LNL-4420 is an Advanced Dual Reader Controller by Lenel that provides a single-board solution for interfacing up to 64 doors, plus auxiliary inputs and outputs, to an OnGuard® system.

- Input/Output Modules

- LNL-1100: Series 3 Lenel® Input Control Module (ICM) provides the access control system with high-speed acknowledgement of critical alarm points in monitored areas.

- LNL-1200 Series 3: Lenel® Output Control Module (OCM).  16 Form-C 5 A, 30 VDC contacts for load switching, 2 dedicated digital inputs for tamper and power failure status, Elevator control, support for 128 floors, Advanced Encryption Standard (AES) 128-bit or 256-bit encryption.

- Reader Interface Unit

- LNL-1300 Series 3: Single Reader Interface (SRI) Module. Access control card readers, keypads, or readers with keypads that use standard Wiegand Data1/Data0, Supervised or Unsupervised F2F, or Clock/Data communication are supported, as are those supporting the bidirectional RS-485 Open Supervised Device Protocol (OSDP™). 12 or 24 VDC power supply, Two Form-C relay outputs (5 A door strike and 1 A aux relays), Up to 16 different card formats, Door contact and REX open or closed, supervised or non-supervised, Strike control output.

- LNL-1320 Series 3: Dual Reader Interface (DRI) Module: Access control card readers, keypads, or readers with keypads that use standard Wiegand Data1/Data0, Supervised or Unsupervised F2F, or Clock/Data communication are supported, as are those supporting the bidirectional RS-485 Open Supervised Device Protocol (OSDP™). 12 or 24 VDC power supply, six Form-C 5 A at 28 VDC relay outputs, up to 16 different formats, door contact and REX open or closed, supervised or non-supervised, strike control output, dedicated tamper and power failure circuits, on-board regulator allows 12 VDC reader support from 24 VDC power source

- LNL-8000: The Star Multiplexer from Lenel is designed to implement star topology on a downstream port of any Lenel® Intelligent System Controller or on any host communication port of any OnGuard® server.  Up to eight RS-485 (2-wire) connections or four RS-485 (4-wire) connections can be made downstream of the LNL-8000. Host communications - 38.4 kbps direct wire (RS-232/RS-485 multi-dropped), 12 VDC input power, Status LEDs for heartbeat, upstream and downstream communication.

  - Appendix L – Approved Intrusion Detection Equipment

- Control Panel

- Bosch B9512G Control Panel Alarm Panel for intrusion devices: Burglary, Commercial Panel has 599 individually identified points, 32 areas.  ULC listed.  To be used in combination with Bosch B426 Conettix Ethernet Communication Module and/or application appropriate B44x cellular communicator module.  Each Bosch panel shall have a minimum of 2 paths of communication to support 3rd party monitoring and integration with Lenel OnGuard.

- Keypad

- Bosch B942 Touch Screen Keypad for office and corporate sites.

- Bosch B930 ATM Style-Alphanumeric keypad (SD12) for environmental services non-office facilities.

- Input / Output Modules

- Bosch B208 SDI2 8-Input Expansion Module connects to a control panel through the SDI2 bus.  This module is supervised and communicates back to the control panel all point status changes.  The module’s expansion points operate the same as the points on the control panel.

- Bosch B308 SDI2 8-Output Expansion Module.  The B308 Octo-output Module provides eight programmable outputs.  Each relay provides dry contact switching rated for 1.0 A at 5-24 VDC.  The outputs are accessed through on-board screw terminal connections.  The B308 is compatible with the SDI2 bus.  The onboard switches are used to specify module addresses.  Control panel programming will determine output response to specific events.

  - Appendix M – Approved Intercom Equipment

- TOA Electronics

- TOA N8000 IP intercom system.  Master Intercom N-8500MS with 32-character LCD display and Q-N-8540WP Outdoor Door Station.  These devices are Power Over Ethernet (“POE”) and connect directly to the building LAN via POE network switch.  Include YC-280 wall mount bracket for Master station and either flush mount back box model YC-150 or surface mount back box YS-13A depending on application.

- Valcom

- Valcom model VIP-172AL IP DoorPhone/Intercom: The VIP-172AL IP Talkback Door phone/Intercom allows communication to Valcom FXS units (VIP-811, -812, -814) and SIP Based telephone systems via an IP-based network.  PBX, FXO Port w/VIP-811, POTS telephone set w/VIP-811, Valcom M Cast Page Group, SIP – enabled telephone system, RJ-45 for network connection, 1 Form C relay, Power over Ethernet (PoE) 802.3af compatible.

  - Appendix N – Approved Credential and Credential Reading Equipment

- Multi-Technology iCLASS Reader

- Card Readers: Provide multi-technology HID® multiCLASS SE® proximity card readers where shown on the Drawings and/or where required by the Contract.  Card Readers shall be rated for indoor and outdoor use, have multicolour LED with beeper for operator status indications and will operate on 5-16 V DC.  Provide thin line mullion style readers where required to match door frame configuration.

- HID Corporation, HID® multiCLASS SE® proximity card reader RP15/RP40/RPK40, configured to work with all Regional credentials.

- Proximity Card

- Proximity Cards used by the Region are HID Corporation ProxCard II, HU-1326LSSSV (i.e., 120 kHz, 26 bit).

The Contractor is not required to supply proximity cards to the Region unless otherwise indicated.

- Long Range Card Reader

- Long range proximity card reader, typical read range 3 to 5 metres

- HID® Proximity MaxiProx® 5375.

- Nedap 9215689 TRANSIT Ultimate.  To be utilized for motorized entrance gates at the following facilities (to be identified in the York Region design drawings) with the prior approval from the Region:

  - Transit Bus Storage Facilities

  - Roads and Traffic Operation Yards

- Long Range Proximity Tag

- Long range proximity card, 860 – 960 MHz proximity active vehicle tag.

- HID Corporation, SIO Enabled UHF/iCLASS Smart Card.

- Nedap 9882650 Window Button R/O.  To be utilized for motorized entrance gates at the following facilities (to be identified in the York Region design drawings) with the prior approval from the Region:

  - Transit Bus Storage Facilities

  - Roads and Traffic Operation Yards

  - Appendix O – Miscellaneous Security Devices

- Door Contacts

- Magnetic door contacts.

- 1” recessed steel door approved door contact as shown in the list in Appendix J - List of Approved Security Equipment.  Overhead door contact as shown in the list in Appendix J - List of Approved Security Equipment to be installed off the ground.  Alternative solution might be required based on door type, mounting requirements, and environment.

- Explosion Proof door contacts or Intrinsically Safe devices as shown in the list in Appendix J - List of Approved Security Equipment to be used in Class 1, Div.1 and Div.2 classified areas.

- DPDT door contacts shall be used at facilities with Intrusion Detection integration requirements.

- Rechargeable Lead-Acid Batteries

- 12V 7Ah Sealed Lead Acid Battery

- Ultratech, Honeywell, Detection Systems, Bosch-Canada, or approved equivalent.

- Exit Devices / Panic Bars

- Push pad exit device, dull chrome finish, UL Listed Von Duprin Panic Hardware FVSR SA163 (N), tested in accordance to ANSI A156.3, 1989, Grade 1.

- Von Duprin 99K-NL Series Panic Exit Devices, or approved equivalent.

- Electric Door Strikes

- Heavy duty, stainless steel construction, 3000 lbs static strength, UL 1034, ANSI/BHMA Grade 1, 0.25 Amps @ 24 VDC.

- HES 1006 Series Electric Strike or approved equivalent.

- HES 9600 Series Electric Strike, or approved equivalent.

- Electrical Power Transfer

- Transfer of electrical power from door frame to the edge of a swinging door; two (2) 18 AWG wiring, 24VDC, 2A continuous, 16A maximum surge.

- Von Duprin EPT-2, or approved equivalent.

- Control Transformers

- 120V input, 16V output, 40VA, 60 Hz, single phase rating, copper conductors, dry type.

- Transformers shall be designed, constructed and rated in accordance with UL, CSA and NEMA standards.

- All transformers for each project shall be from the same manufacturer.

- ATC Frost Magnetic Inc., 1640, or approved equivalent.

- Request to Exit Sensors

- Wall mount high impact ABS plastic enclosure, alarm output: form “C” contact, single or double door use, adjustable to 60 s, UL Listed.

- Honeywell Model IS310

- Push Buttons

  - Exit Push Button

- Wall mount brushed stainless steel plate enclosure, momentary switch output, SPDT 10A @ 125/250 VAC, UL Listed.

- Tyco Security Products - Kantech PB-EXIT, or approved equivalent.

  - Arming Push Button

- RCI R991RBPTD9 Wall mount brushed stainless steel plate enclosure, push button with pneumatic time delay (adjustable 0-45 seconds), blank red button.

- Glass Break Detectors

- Shall detect breakage of plate, tempered, layered, laminated and wired glass types, complete with automatic environment test circuitry, detection range of 9 metres, alarm contact 50mA @ 24VDC, UL Listed.

- Honeywell FlexGuard FG-1625F, or approved equivalent.

- Motion Detectors

- Wall mount motion monitor with temperature compensation, high impact ABS plastic enclosure, alarm output: form “C” contact, 125 mA @ 28 VDC, tamper and trouble output contacts, UL Listed.

- Detection Systems DS940Q.

- Optex DX40.

- Approved equivalent.

- Audio Annunciator

- Wall mount, 24 VDC, 100 dB @ 10’, UL Listed.

- Toxalert Inc. HORN/REM RH-24 VDC, or approved equivalent.

- Uninterruptible Power Supply

- APC Back-UPS Pro to power all security, access control and wireless network solution.  Model to be used is Antigen-presenting cell (“APC”) Pro BR1500G or approved equivalent.

- The UPS must reside on a dedicated AC circuit fed from an emergency power panel wherever possible.

  - Appendix P – Digital Video Management System

- Digital Video Management System (DVMS)

- Lenel Milestone XProtect® Expert Digital Video Management System.  The Digital Video Management System (DVMS) shall be designed and developed in conformity with the following standards:

ISO 9001 (2015) Quality management systems

ISO/IEC 15504 Measurement Framework for Process Capability and CMMI Level 3 or higher (Capability Maturity Model Integration) (SPICE 2.0 Software Process Improvement and Capability dEtermination)

SEI CMM Level 3 or higher (American Software Engineering Institute - Capability Maturity Model)

The Digital Video Management System shall include:

Database Server(s)

Application Server(s)

Local recording Networked Camera Server(s) with appropriate software and databases as required

Operator Workstations (dedicated to the DVMS)

Network connected cameras and/or network connected video encoders

Continuous Recording capability for a minimum of thirty (30) days at 30 frames per second (note: see more on the attached camera configuration parameters)

- The Digital Video Management System (“DVMS”) shall be capable of supporting unlimited number of cameras.

As a minimum, the system must support all the latest Axis network cameras, encoders and camera streamers.

- The following DVMS equipment must be used:

Camera Streamers / Video Encoders:

AXIS Communications

PTZ Network Cameras:

AXIS Communications Q6075-E

Fixed Indoor Dome Cameras:

AXIS Communications P3375-LV

Fixed Outdoor Dome Cameras:

AXIS Communications P3375-LVE

Fixed 360 Indoor/Outdoor Camera:

AXIS Communications P3717-PLE

Use the latest generation of the equipment mentioned in this paragraph.  The contractor must ensure that all equipment which is being supplied will be compatible with the existing and previously installed components.  If any modifications or upgrades are required, these changes must be included in the project budget and identified in the proposal.

- The DVMS shall support at least the industry-standard Motion JPEG, MPEG-4, H.264, and H.265 as well as Axis’s Zipstream technology encoding formats.

- The DVMS system shall be fully integrated with the Lenel OnGuard version currently in use by York Region and be fully compatible with all announced Versions of OnGuard at the time of installation.  Lenel OnGuard will be used as the primary user interface.

- Network and Video Cabling

- A Local Area Network (LAN) shall be provided for communication between the system elements.  All interfaces to the LAN shall be a minimum of 1000BaseTX Ethernet.  The LAN may use additional technologies within the backbone for greater speed or distance.  Acceptable types are:

  - FDDI (Fibre Distributed Data Interface)

  - 1000BaseSX or 1000BaseLX Gigabit Ethernet (fibre)

  - Asynchronous Transfer Mode (ATM)

  - 1000BASE-TX

- The LAN shall use standard network cables.  Acceptable cable types are:

- Optical Fibre

- Category 6 or greater Unshielded Twisted Pair (UTP)

- The LAN shall be logically and/or physically separate from any existing LAN infrastructure.  Interconnection to other LANs shall only be through one of the following:

- A router

- A Layer 3 capable network switch

- As an additional VLAN to the existing LAN equipment.  Where required to interconnect VLANs, a router or Layer 3 capable switch shall be provided by the contractor.

- Network video cables shall not be run back to the Camera Server individually.  All communications with the Camera Server shall be via the LAN.  Each network camera or video streamer shall have a single network interface which is to be used for video and also Pan/Tilt/Zoom communications.

- Supply a complete and working Closed-Circuit Television System (CCTV) System and Digital Video Management System (DVMS).

  - Appendix Q – Conduits, Fittings and Accessories

- Conduit, Fastenings and Fittings

- Comply with the latest proclaimed version of the OESC.

- Rigid PVC conduit:  Conduit, including elbows and fitting, Schedule 40 wall thickness, solvent weld connections, by IPEX Inc., Carlon or approved equivalent.

- Rigid PVC conduit connectors:  Adapter type with threaded male portion, by IPEX Inc., Carlon or approved equivalent.

- Conduit straps for rigid steel and PVC conduit:  Malleable iron, hot-dip galvanized, single hole type for conduits up to 50 mm, two-hole type for conduits larger than 50 mm.

- Beam clamps:  Hot dip galvanized steel designed to clamp onto both sides of the flange.  Cat. #S997BC-HG (100-230 mm flange) by Sasco Tube & Roll Forming Inc., Cat. #S999BC-HA (175-430 mm flange) by Sasco Tube & Roll Forming Inc., or type CS91 by Construt Inc. or approved equivalent.

- Expansion couplings:  With ground straps or clamps.  Type XJ by Cooper Crouse-Hinds Canada or approved equivalent.

- Swivel couplings:  Threaded, one piece, by Elliot Electrical Manufacturing Co. Running threads are not acceptable or approved equivalent.

- Conduit spacers:  Malleable iron, sized to suite conduit size, by O-Z/Gedney Co., or 1300 Series by Thomas & Betts Ltd or approved equivalent.

- Conduit seals and fittings for hazardous locations:  Suitable for applications in designated area, by Crouse-hinds, Pyle-National of Canada Inc., Killark Electrical Manufacturing Co., Appleton Electric Ltd., O-Z/Gedney Co., or approved equivalent

- Hazardous area seal filling compound:  As recommended by seal manufacturer.

- Pull cords:  6 mm polypropylene or nylon material.  Pro-pull rope by Ideal Industries Inc. or approved equivalent

- Bituminous backpaint:  In accordance with CAN/CGSB-1.108.

- Conduits and all junction boxes shall be colour coded to identify the nature of the cabling which is contained within.  Where it is not practical to paint the entire conduit, pull box or junction box, e.g., PVC devices, suitable coloured markings shall be applied and visible from a distance, e.g., boxes on the ceiling shall be visible from the ground.

| Sequence No. | Voltage | Colour |
| --- | --- | --- |
| 1 | High Voltage (In Excess Of 750 V): | Brown |
| 2 | 347/600 V: | Sand |
| 3 | 120/208 V: | Grey |
| 4 | Emergency Power: | Associated Voltage Colour |
| 5 | Fire Alarm & Fire phone: | Red |
| 6 | Security/Intrusion/Surveillance: | Green |
| 7 | Low Voltage Switching: | Black |
| 8 | Annunciator Cabinets: | Black |
| 9 | Data/Telephone Cabinets: | Blue |
| 10 | Telephone Backboards: | Grey |
| 11 | Television: | White |
| 12 | Public Address/Intercom: | Purple |

- York Region Convention for Conduit Colours:

.

Cable Colours are not specified unless they are defined for a particular project

  - Appendix R – Cabling, Conductors and Miscellaneous Accessories

- Wiring and Miscellaneous Accessories

- Provide all RS-232, RS-485, Optical Fibre and Ethernet cabling, and Fibre and Ethernet jacks as required for a complete network, as applicable.

- Direct burial cable for all outdoor applications.

- Cabling

- RS-485 Cables

  - Belden EIA Industrial RS-485.

  - Conductors:  Twisted pair, each conductor No. 22 AWG stranded copper.

    - Pairs: 2.

    - Shield:  Aluminum-polyester and 90% copper tinned braid.

    - Jacket:  Black UV resistant PVC.

    - Electrical Characteristics at 20oC

      - Capacitance:  36.1 pF/m

      - Impedance:  120 ohms

      - Propagation Velocity:  78%

    - Belden Datalene Insulated 3107A.

- Lenel hardware wiring shall follow the wiring guide below:

| Purpose | Cable type | Gauge | Cond. | Description | Belden number |
| --- | --- | --- | --- | --- | --- |
| RS-485, 4-wire | Non-plenum | 24 | 2P | Overall shield | 9842 |
| RS-485, 4-wire | Plenum | 24 | 2P | Overall shield | 88102 |
| RS-232 | Non-plenum | 24 | 5 | Overall shield | 9610 |
|  | Plenum | 24 | 6 | Overall shield | 83506 |
| Reader drops | Non-plenum | 22 | 6/8 | Overall shield | 5504FE/ 5506FE |
|  | Non-plenum | 22 | 6 | Overall shield | 5504FE, |
|  |  |  |  |  | 9536 |
|  | Plenum | 22 | 6/8 | Overall shield | 6504FE/6506FE |
| 12 VDC power | Non-plenum | 18 | 2 | Overall shield | 5300FE, 8760 |
|  | Plenum | 18 | 2 | Overall shield | 6300FE, 88760 |

- CAT6 Cables

  - Conform with the following plenum rated Ethernet 1000BASE‑TX TIA/EIA 568-B.2-1 Category 6 cable:

    - CSA Certified for trays and risers.

    - Conductors: Unshielded twisted pair, #23 AWG solid copper.

    - Pairs: 4

    - Jacket: Purple Flamearrest, CSA FT4/FT6 rating.

    - Certification/Testing to at least Category 6 in accordance with the current TIA/ISO Channel Standards.

    - Belden Inc. #2400 or approved equivalent.

- Instrumentation Cables (4-20mA)

  - Belden Inc. #8760 or approved equivalent.

    - #18 AWG.

    - 16-stranded copper.

    - Beldfoil aluminium polyester shield.

    - Twisted shielded pair.

    - Bare #20AWG copper drain wire.

- Wiring Accessories

- Wire and cable markers:  Printable, self-laminating, self-adhesive markers, white background, black lettering on white background, vinyl plastic or polyester film suitable to environment.  Wire marker to be sleeved with clear heat shrink tubing.

- Terminal blocks:  600 V, 25 A minimum rating, modular, 35 mm DIN rail mounted, provision for circuit number labelling, individually removable, sized to accommodate conductor size and circuit current.

- SAK Series by Weidmuller Ltd.,

- UK Series by Phoenix Terminal Blocks Ltd.,

- WK Series by Wieland Electric Inc.,

- ABB Entrelec or

- Approved equivalent.

- Field wiring terminations:  Where screw-type terminal blocks are provided, supply insulated fork tongue terminals.

- Sta-Kon by Thomas & Betts Ltd.,

- Scotchlok by 3M Canada Inc or

- Approved equivalent.

- Moisture and waterproofing:  In wet locations, with Liquid Tape by Ideal Industries Canada Corp. or approved equivalent.

- Cables ties:  Nylon, one-piece, self-locking type, by

- Thomas & Betts Ltd.,

- Burndy Inc.,

- Wieland Electric Inc or

- Approved equivalent.

- Electrical insulating tape:  Scotch 33 by 3M Canada Inc or approved equivalent.

- Cable grips:  To accommodate type and geometry of cable supported, single weave, variable mesh design, by:

- Thomas and Betts Ltd.,

- Crouse Hinds,

- Woodhead Canada Ltd or

- Approved equivalent.

- Cable pulling lubricant shall be compatible with cable covering and not to cause damage or corrosion to conduits or ducts.  Yellow77 or Clear-Glide by Ideal Industries Canada Corp. or approved equivalent.

- Input 120 VAC power to all security related and access control panels must be provided at each location identified in the design drawings and must be dedicated and separated from any other loads.

- Where conduits may be accessible to “rodents”, or if gas seepage is a risk, steps should be taken to block such rodents from entering and damaging cable insulation.  The contractor shall ensure that the proposed products do not prejudice the cables which are installed in the conduits (or ducts).  Possible products include:

- Polywater Conduit/Duct Seal,

- 3M Scotchcast Duct Sealing Kit,

- Filoseal + HD Duct Sealing Kit or

- Approved equivalent.

- Wherever conduits or cables are installed through fire rated elements the contractor is responsible to repair any damage to the impregnability of the wall in conformity with the Code requirements.

- Communications Line Extenders

- When communications lines are subject to interference from electrical noise, as for example, when using travelling lines intended for power transmission to elevator cars or lines passing through elevator mechanical rooms, precautions are needed to avoid the introduction of erroneous data.

- Products provided by Cypress Integration Solutions have been proven to allow Wiegand signals to maintain their integrity under onerous conditions and are to be used for the Region under such circumstances.

- The recommended device is the Suprex RS-485, Single Reader Extender SPX-1300.  2 modules are required, one at the computer end and one in the elevator and both will require power.

  - Appendix S – Parking Barriers

- General Observations

- There are currently no specified manufacturers or models for the following items:

- Detector Loops

- Detector loop sealants

- Loop Amplifiers

- Barrier Arms

Full details of the proposed equipment must therefore be provided for each project.

  - Appendix T – Locks

- Keys and Cylinders

- All doors are to be equipped as outlined in the Security Device Summary document which is associated with the current project.  The final configuration will require that the construction (temporary) lock cylinder cores will be replaced with Medeco M3 IC cores.  Where specific locks are not defined, doors should initially be equipped with:

        - Sargent,

        - Assa Abloy or

        - Corbin locksets.

- All interior pedestrian exit doors (not overhead doors) shall be equipped with either a “push paddle” or a “panic crash bar” exit device.  Such devices shall be installed at a standard height.

- For ALL Environmental Water and Wastewater facilities Medeco M3 Logic Cylinders shall be used for all exterior doors, and doors that need to be secured.  All door hardware must be compatible with Medeco M3 Logic Cylinders.

- Electromagnetic Locks

- As is stated elsewhere electromagnets may be used on York Region projects where specified.  Such installations require permits and integration with the Fire Alarm system.

- The Hold Force Sensor should be wired to the door controller if the controlled allows for an auxiliary connection to this sensor or may be wired in series with the door contact so that in either case the Intrusion Detection System will report that the door is improperly closed.

- Note that in the event that the power to the magnet fails and the door remains closed, the HFS will report the door as being “forced”.

- It is recommended that the electromagnet should be installed with the factory installed door position indicators and LED status indicator.

- The Contractor shall reinforce the door and, as required the door frame, to ensure that neither will distort sufficiently to allow the door to open because of a mechanical misalignment.

- The Pre-Approved Electromagnetic Lock is:

      - RCI (Dormakaba) Model 8310 (single door) and Model 8320 (double door) with auto sensing 24 / 12 V DC and LED Status indicator.

      - Brushed Aluminum by default but optional finishes are available.

      - Optional Door Status Senor (DSS), i.e., Door Contact.

      - Optional Security Condition Sensor (SCS), i.e., Bond Sensor.

  - Appendix U – Universal Washroom

- Available Washroom Kit

- The approved hardware required to implement the Universal Washroom in compliance with the OBC is

Camden Door Control equipment package CX-WEC10, “Universal Emergency Call System Kit” which includes: Emergency Button, LED Annunciator with sounder, Dome Light (various colours) with sounder and sign.

  - Appendix V – Labelling

- Introduction

- This section describes the requirement for the Contractor to suitably identify and label all pieces of equipment.

- ANSI/TIA-606-C is the current version of the voluntary standard for administering telecommunications cabling infrastructure, released by the Telecommunications Industry Association (TIA) in July 2017.  TIA-606-C builds on the guidelines already established in TIA-606-B, released in 2012, as well as includes some new additions and updates.  This standard provides extensive guidelines to the proper use of labelling for environments such as that used at York Region.

- The primary objecting of the labelling is to ensure that all those charged with the responsibility of performing maintenance or repairs on the system at any time can uniquely and safely refer to each component of the system.

- The labelling shall always correspond with the terminology and format of the labels defined on the drawings.  Labels shall always be applied to every serviceable or adjustable component of the system.

- Details related to the labelling should always be presented to York Region before being applied.

- Depending on the installation, there will be equipment cabinets, junction boxes, pull boxes, man holes, cameras, network components and other components which are installed to support the security system.  Each of these “devices” must be labelled clearly and permanently, using the same nomenclature than has been documented in the system schematics.

- Typically, the preferred form of permanent labelling is engraved Lamacoid.  The colours and the format of the label shall be approved by York Region and shall follow the guidance of this section.  The selection of colours should be designed so that the engraved or printed labels exhibit good contrast and will not fade or deteriorate due to exposure to the environment in which they are installed, e.g., sunlight or de-icing chemicals.

- The labels, Lamacoid or flexible cable labels shall not, inherently or through their means of installation, induce damage or corrosion to the surface to which they are being attached.

- There will be situations where other means of labelling devices may be more suitable and such options should be reviewed with York Region.

- The labels shall be screwed to the cabinets or, at the discretion of York Region, may be attached to the cabinet using a suitable double-sided weatherproof tape.  The surfaces to which the tape is to be applied shall be properly prepared if this approach is selected.  All labels to be attached in this manner shall be in “landscape mode” and centred from left to right.

- In some situations, labels will need to be “hung” directly from a component, and this may be accomplished by means of a hole drilled into the label and the use of suitable stainless-steel aircraft cable made for this purpose.

- Further a suitable colour code which may be implemented on conduits with a colour band or in the labelling is recommended.  (See Appendix Q: Conduits, Fittings and Accessories)

- All labels shall be machine-generated.  Handwritten labels are not acceptable.

- All cables and conductors shall be labelled at each end and at each pull box or hand-hole.

- All labelling shall be consistent on site, in the as-built documentation and in the software.

- Special care should be exercised and labels should be applied to provide warnings related to special procedures when opening some “devices”.  For example, if there are multiple sources of power, potentially dangerous supervision of, or monitoring of, automated responses to “tampering” etc. notifications should be present to advise the service staff of such situations.

- The contractor shall post warranty/contact information on the inside of the main control enclosure for each facility as well as the commissioning date.

- Labelling Details

- Details with respect to the information to be included within the labels are provided below.

- Main alarm outputs and relays shall be labelled accordingly.  All alarm points, card readers and other system components shall be labelled in accordance with the door numbering and description syntax.

- Enclosures

- Electrical cabinets shall be identified with at least:

• Voltage, type of power, power source (including as appropriate Circuit No);

• Purpose of the cabinet; and

• Name of the cabinet as shown on the drawings.

- Communications / Security cabinets shall be identified with at least:

• Type of Application, Signal source (including as appropriate Circuit / Port No);

• Purpose of the cabinet; and

• Name of the cabinet as shown on the drawings.

- Junction boxes shall be identified with at least:

• Nature of enclosure content, e.g., Data, CCTV, Power, etc

• If appropriate, Voltage, type of power, power source (including as appropriate Circuit No);

• Purpose of the cabinet; and

• Name of the cabinet as shown on the drawings.

- The Contractor shall label all enclosures containing security equipment indicating the nodes installed within.

- All Networked equipment is to be labelled with corresponding IP information.

- Conduits

- The following information is repeated here for the sake of convenience and also appears in Appendix Q: Conduits, Fittings and Accessories.

- York Region uses the following Conduit colours:

| Category No. | Voltage | Colour |
| --- | --- | --- |
| .1 | High Voltage (in excess of 750 V): | Brown |
| .2 | 347/600 V: | Sand |
| .3 | 120/208 V: | Grey |
| .4 | Emergency Power: | Associated Voltage Colour |
| .5 | Fire Alarm & Fire phone: | Red |
| .6 | Security/Intrusion/Surveillance: | Green |
| .7 | Low Voltage Switching: | Black |
| .8 | Annunciator Cabinets: | Black |
| .9 | Data/Telephone Cabinets: | Blue |
| .10 | Telephone Backboards: | Grey |
| .11 | Television: | White |
| .12 | Public Address/Intercom: | Purple |

- Cable Colours are not specified unless they are defined for a particular project.

- Cables

- Each end of every cable including the grounding system shall be labelled.  Every cable shall also be identified at every pull box or other accessible location along the length of the run.

- These labels shall be of the “wraparound” variety, and as for all other labels shall be machine-generated.

- The labels shall be of suitable size to fit the cables to which they are applied i.e., there will generally be a requirement for multiple label sizes.  The labels shall be PANDUIT PLL-33-Y3-5 labels or approved equivalent.

- The specific cable label types are designated based on diameters anticipated for a project.  It is recognised that some of the cable diameters may be changed during project execution and for this, or other reasons, the Contractor shall ensure that the overall requirement to ensure that the clear part of the cable label protects the printed part of the cable label is always satisfied.  This specification may demand alternative cable labels which shall be from the PANDUIT PLL product line or approved equivalent.

- The label shall be applied within 15 cm (6 ins) of the end of the cable and shall be located so that the cable may readily be identified.

- The printing shall be at least 12-point Arial font or approved equivalent.

- All labelling must be mechanically printed using a laser printer and follow the ANSI/EIA/TIA-606C guideline for colour codes.  Hand written labels are not permitted.  The following identifies the labelling convention.

- Cable Labelling Conventions

- The labelling of cables shall clearly identify the application of the cables.  This convention requires that cables be identified as follows:

• C for communications;

• F for fire related applications;

• H for “high”-voltage power (greater than 48V);

• L for “low”-voltage power (less than 48V);

• N for networking;

• S for signalling;

• T for transducer; and

• V for video cables.

- A typical cable label might, for example, be labelled as: 
“L0003-GAR001-064-ADMIN009-922”.  Which would signify,

- Low Voltage Cable

- Number 0003 cable

- Cable is from location “GAR001”, “connection 064” to location “ADMIN009”, “connection 922”, i.e., source and destination must be uniquely specified.

- Such cable identifications shall be incorporated in the documentation.

- The Contractor shall obtain the York Region’s approval of any modification or extension to this convention.

- Main alarm outputs and relays shall be labelled accordingly.  All alarm points, card readers and other system components shall be labelled in accordance with the door numbering and description syntax.

- Considerations Regarding ANSI / TIA-606-C:

- TIA-606-C is the latest update to the voluntary standard for administering telecommunications cabling infrastructure, released by the Telecommunications Industry Association (TIA) in July 2017.  TIA-606-C builds on the guidelines already established in TIA-606-B, released in 2012, as well as includes some new additions and updates.

- How to Properly Identify Cables According to TIA-606-C

- Each of the following components must be clearly labelled with the appropriate identifiers:

- Pathways

- Work area outlets

- Patch panels

- Racks and cabinets

- Ports

- Grounding busbars

- Cabling

- Firestop locations

- Telecommunications space

- Data center room grid

- Examples of TIA 606C Compliant Labelling (Brady Labels)

    - LINK Identifier Not Terminated in the Same Space Label Example

    - LINK Identifier Terminated in Same Space Label Example

    - Patch Panel Identification Label Example

  - Appendix W – Sample Graphic Alarm Map, Regional Layout and Icons

- INDEX

1, 2, 3, …

1000Base-LX Gigabit Ethernet 	 123

1000Base-SX Gigabit Ethernet 	 123

1000Base-TX Gigabit Ethernet 	 34, 36, 123

360° Surveillance Cameras 	 27

3rd Party Monitoring Station Communications 	 49

3rd Party Notification Verification 	 57

A

Abbreviations, Standardised 	 103

AC Fail Battery Trouble, Status Offline 	 14

AC Fail, Power Failure, AC Restore, Power Restore 	 14

AC Restore, Power Restore, AC Fail, Power Failure, 	 14

Acceptance Activities, Proposed Testing and 	 16, 17, 22

Acceptance Testing, Final 	 18

Access Card Management Issues 	 20

Access Control and Intrusion Detection, Integration of 	 12

Access Control and Intrusion Detection, Security 	 23

Access Control and Parking Barrier, Integration of 	 39

Access Control Architecture, Elevator 	 31

Access Control Components 	 112

Access Control Detail, Door Type T5 Overhead 
Garage Door with 	91

Access Control Elevator Fire Alarm 	 31

Access Control Elevator Power Failure 	 31

Access Control Equipment, Approved 	 114

Access Control Integration 	 7

Access Control Integration, Elevator 	 30

Access Control Interface, Dynamic Icons on 	 12

Access Control Intrusion Detection Integration 	 9

Access Control of Barrier Arms 	 38

Access Control System Alarm Monitor 	 13

Access Control System User Interface 	 9

Access Control System Value Added Resellers 	 110

Access Control, Bypass Switch for Elevator 	 34

Access Control, Limitations in Elevator 	 31, 34

Access Control, Multi Tenant Elevator 	 34

Access Control, Scheduling Elevator 	 34

Access Control, Video Integration with 	 28

Access Granted 	 52

Access Granted Denied and Reason, Card Activities 	 12

Access Intrusion System Components, Security 	 86

Access Levels 	 14

Access Levels for Elevators 	 34

Access Levels, Local 	 52

Access Levels, Regional 	 52

Access, Gate 	 7

Access, Locked Floor 	 31

Accessories, Cabling Conductors and Miscellaneous 	 126

Accessories, Conduits Fittings and 	 124

Accessories, Conduits, Pathways, Fittings, Cables, 	 37

Accessories, Wiring 	 128

Accessories, Wiring and Miscellaneous 	 126

Accessory Cables 	 56

Acid Batteries, Rechargeable Lead 	 119

Acquisition, Equipment 	 6

Acronyms, Standardised 	 103

Across Region, Consistent Functionality 	 11

Activation and Deactivation, Schedule 	 12

Activation, Entry and Reset Vehicle Detection Loop 	 39

Active On Schedule, Status Unlocked Tamper Faulted 	 14

Activities Access Granted Denied and Reason, Card 	 12

Activities, Proposed Testing and Acceptance 	 16, 17, 22

Activity Logging, Parking Barrier 	 39

Adapters and Controllers 	 22

Additional Infrastructure 	 21

Additional Parts, Contractor 	 44

Address Requirements, IP 	 47

Addresses for Hardware Modules and Points 	 23

Addresses Starting from, Sequential 	 9

Addresses, Reserved 	 9

Addresses, Switch Settings 	 23

Addressing Charts 	 9, 16, 17, 22

Adherence to Labelling Standard 	 136, 137

Administration Manuals, System 	 17

Administration of System, Regional 	 20

Administrative Functions 	 17

Administrator, Security System 	 57

Administrators, System 	 14

ADO, Automatic Door Operators 	 51

ADO, Sequence of Operation 	 51

Advice, Expert 	 20

Affected by Camera Stability, Picture Quality 	 25

Affected by Vibration, Image Quality 	 25

After Adjustments, Retesting 	 18

Against Condensation, Protection 	 45

Air Conditioning 	 9

Air Temperature, Ambient 	 109

Alarm Annunciation on All Keypads 	 13

Alarm Keypads, Annunciator 	 13

Alarm Map, Sample Graphic 	 139

Alarm Monitor, Access Control System 	 13

Alarm Monitoring 	 7

Alarm Monitoring Software Client 	 12

Alarm Monitoring Software Client Application 	 13

Alarm Monitoring, Universal Washroom 	 42

Alarm Notification, Wireless 	 49

Alarm Points 	 16, 17

Alarm Points, Contacts for 	 49

Alarm Points, Naming of 	 49

Alarm Points, Response Plan for 	 49

Alarm Rate FAR, False 	 24

Alarm Reports, Trouble and 	 12

Alarm System Contractor, Fire 	 47

Alarm Types to be Monitored Off-Site 	 49

Alarm, Access Control Elevator Fire 	 31

Alarm, Duress 	 14

Alarm, Facility Wide 	 57

Alarm, False 	 24

Alarm, Instant 	 13

Alarm, Intrusion 	 53

Alarm, Nuisance 	 24

Alarm, Panic 	 7, 14, 42

Alarm, Region Wide 	 57

Alarm, Test 	 49

Alarmed Forced Held Open Locked, Status Normal 	 14

Alarmed Forced Held Open, Status Armed Disarmed 
Normal	13, 14

Alarms for Each Facility, Custom 	 13

Alarms for Each Site, Custom 	 13

Alarms, Arming Trouble 	 12

Alarms, Emergency Button 	 42

Alarms, Life Safety 	 7

Alarms, Local 	 57

Alignment, Raceway Conduit 	 43

All Equipment, Labelling of 	 133

All Keypads, Alarm Annunciation on 	 13

Allowed Modifications 	 11

Alternative Products 	 24

Ambient Air Temperature 	 109

Amplifiers, Vehicle Detection Loop 	 40, 130

Analogue, Digital Cameras 	 27

Analyst, Business System 	 21

Announced Enhancements, Compatibility with 	 28

Annunciation on All Keypads, Alarm 	 13

Annunciator Alarm Keypads 	 13

Annunciator, Audio 	 121

Antenna, Exterior 	 21

Anti Passback Parking Operation 	 39

API SDK, Video Recording System 	 30

Apparatus, Simple 	 111

Appendices 	 6

Appendix List 	 59

Applicable Codes and Jurisdictions 	 11

Applicable Standards 	 11

Applicable to Security Projects, Standards, Codes 	 77

Application and Database Integration 	 18

Application Programming 	 11

Application, Alarm Monitoring Software Client 	 13

Applications, LAN for Security 	 34, 37

Applications, Manufacturer Supplied 	 12

Approval by York Region, Changes 	 10

Approval of Updates, Regional 	 23

Approval, Consultant 	 56

Approval, Equipment Substitution 	 24

Approval, Implementation Plan 	 11

Approval, Training Syllabus 	 20

Approval, Training Syllabus Submission for 	 20

Approval, Upgrade Camera Firmware 	 28

Approvals 	 56

Approved Access Control Equipment 	 114

Approved Cabling Types 	 126

Approved Commissioning Form, Regional 	 61

Approved Credential and Credential Reading Equipment 	 118

Approved Intercom Equipment 	 117

Approved Intrusion Detection Equipment 	 116

Approved Network Devices 	 12

Approved Security Equipment, List of 	 111

Arbiter, Final Submittal Review 	 15

Arc Flash Precautions 	 42

Architectural Floor Plan 	 13

Architectural Specifications 	 41

Architecture of Sites Connected to Main Regional Control Centre 	 8

Architecture, Elevator Access Control 	 31

Architecture, Scalable 	 7

Architecture, Schematic of York Region Security System 	 8

Archiving, Video Image 	 29

Area, Verification of Each 	 53

Areas, Reception 	 7

Arm Disarm Door Operations, Control Functions 	 14

Arm Illumination, Barrier 	 38

Arm Interference Detection, Barrier 	 39

Arm, Breakaway Parking Barrier 	 39

Armed Disarmed Normal Alarmed Forced Held Open, 
Status 	 13, 14

Armed LED Indicator 	 52

Armed, Security System 	 52

Arming and Disarming, Failures 	 12

Arming Button 	 52

Arming Button Card Reader 	 12

Arming Disarming Single Door Detail, Door Type T1 	 87

Arming on Fault, Inhibit 	 57

Arming Push Button 	 120

Arming Restrictions 	 52

Arming Trouble Alarms 	 12

Arming, Exit Delay for 	 12

Arming, Intrusion Detection 	 12

Arms, Access Control of Barrier 	 38

Arms, Parking Barrier 	 130

As-Built Documentation 	 16

As-Built Drawings 	 56

Assemblies, Typical Door Security 	 82

Assembly Drawings 	 23

Assignment, Licence 	 56

Assignment, Location Identifier PIN 	 22

Assignment, Rack Module 	 22

Assignment, Warranty 	 56

Assignments, Module Tag 	 22

Assistance Requirement, Contractor 	 19

Associated Status Disposition 	 13

Assurance, Equipment Substitution Quality 	 98

Assurance, Testing and Quality 	 18

Asynchronous Transfer Mode ATM 	 36

ATM, Asynchronous Transfer Mode 	 36

Audience, Training 	 20

Audio Annunciator 	 121

Audit Trail Log for Entire Site 	 12, 13

Audit Trail Log Verification 	 57

Authorisation from Region, Written 	 11

Authority ESA, Electrical Safety 	 42

Authority Having Jurisdiction, Changes by 	 10

Authority Having Jurisdiction, Working Drawings to 	 10

Automatic Door Operators ADO 	 51

Availability, Overall System 	 54

Available Features 	 17

Available Washroom Kit 	 132

Avoidance Certification, Virus and Malware 	 9

Aware, Made 	 55

B

Back EMF, Suppression of Induced 	 48

Back Plates, Power Supply 	 45

Backbone Interconnection 	 36

Backbone Requirement, Fibre 	 36

Backup and Maintenance Requirements 	 23

Backup Batteries 	 45

Backup Files, Configuration 	 17, 56

Backup, Battery Trouble, 	 14

Bar, Panic Crash 	 40

Barrier Arm Illumination 	 38

Barrier Arm Interference Detection 	 39

Barrier Arm, Breakaway Parking 	 39

Barrier Arms, Access Control of 	 38

Barrier Arms, Parking 	 130

Barrier Free Washroom 	 41

Barrier, Cameras at Parking 	 38

Barrier, Certified 	 111

Barrier, Civil Electrical Communications 
Requirements for Parking 	 40

Barrier, Integration of Access Control and Parking 	 39

Barrier, Physical Protection of Parking 	 40

Barriers, Parking 	 130

Bars, Exit Devices Panic 	 119

Basic Elevator Control 	 30

Basis Testing, Per Function 	 18

Batteries, Backup 	 45

Batteries, Rechargeable Lead Acid 	 119

Battery Labelling 	 14

Battery Trouble, Backup 	 14

Battery Trouble, Status Offline AC Fail 	 14

Bending Radius, Cable 	 43

Bends, Quantity of 	 43

Best Practices 	 6

Best Practices, Wiring 	 46

Bill of Materials BOM 	 22

Bill of Materials, Complete 	 16, 17, 22

Bill of Materials, Contractor 	 44

Black & White Images, Colour and 	 26

Block, Drawing Title 	 82, 84

Blocks, DIN Rail Mounted Terminal 	 46

Blocks, Terminal 	 128

Board, Sequencer 	 51

BOM, Bill of Materials 	 22

Bond Sensors HFS 	 47

Bookmarking, Image Search 	 29

Boundaries, Municipal 	 13

Boxes or Termination, Cable Slack for Pull 	 43

Boxes, Cable Pull 	 43

Boxes, Required Conduits and Junction 	 21

Breach of Contract 	 24

Break Detectors, Glass 	 120

Breakaway Parking Barrier Arm 	 39

Brochures 	 17

Budget, Project 	 24, 28

Buildings, Existing 	 60

Burn-In Image Data 	 29

Business System Analyst 	 21

Button Alarms, Emergency 	 42

Button Card Reader, Arming 	 12

Button, Arming 	 52

Button, Arming Push 	 120

Button, Elevator Floor 	 30

Buttons, Exit Push 	 120

Buttons, Wired 	 7

Buttons, Wireless 	 7

Bypass Switch for Elevator Access Control 	 34

C

Cabinet Capacity, Spare 	 45

Cabinet Components 	 45

Cabinet Labelling 	 48

Cabinet Specifications 	 44

Cabinet, Panel Solutions 	 45

Cabinet, Panel Ventilation 	 45

Cable and Wiring Standard, York ITS 	 34

Cable Grips 	 43

Cable Bending Radius 	 43

Cable Certification Test Results 	 53

Cable Connectors, Watertight 	 43

Cable Dressing 	 54

Cable Grips 	 42, 43, 128

Cable Installation, Headroom for 	 43

Cable Labelling 	 48, 54, 135

Cable Labelling Convention 	 136

Cable Labelling, Examples of 	 137, 138

Cable Labels, Flexible 	 133

Cable Markers 	 43

Cable Markers Labels, Wire and 	 128

Cable Messengers 	 43

Cable OM4, Optical Multi-Mode 	 36

Cable Pull Boxes 	 43

Cable Pulling Length 	 43

Cable Pulling Lubricant 	 43, 128

Cable Pulling Tension 	 43

Cable Separation, Power Communication 	 43

Cable Slack for Pull Boxes or Termination 	 43

Cable Ties 	 128

Cable Trays and Racks 	 43

Cable Warranty, Network 	 54

Cable, Elevator Travelling 	 31, 33

Cables, Accessories, Conduits, Pathways, Fittings, 	 37

Cables, Accessory 	 56

Cables, Installation of Wires and 	 42

Cables, No Oversizing of Conduits or 	 42

Cabling Conductors and Miscellaneous Accessories 	 126

Cabling Segregation in Conduits 	 21

Cabling Types, Approved 	 126

Cabling Warranty Criteria, Lifetime 	 54

Cabling, Network and Video 	 34, 123

Cabling, Shared Pathways for Communications 	 34

CAD PDF Source Files 	 13

Calibrated Wiring Tester 	 53

Calibration Units 	 56

Camera CODEC, JPEG, MJPEG, H.264, H.265, Zipstream 	 28

Camera Compatibility with Installation 	 28

Camera Configuration 	 27

Camera Emulation Software 	 27

Camera Encoders 	 27

Camera Firmware Approval, Upgrade 	 28

Camera Imaging, Direct Sunlight Impact on 	 26

Camera Modelling Software 	 27

Camera Passwords 	 37

Camera Simulation Software 	 27

Camera Stability, Picture Quality Affected by 	 25

Camera Streamers 	 27

Camera, Pan Tilt and Zoom PTZ 	 27, 123

Camera, Stability of 	 25

Camera, Vibration of 	 25

Cameras at Parking Barrier 	 38

Cameras, 360° Surveillance 	 27

Cameras, Analogue, Digital 	 27

Cameras, Fixed Lens 	 27, 28

Cameras, Infra Red 	 26

Cameras, Low Light 	 26

Cameras, Multi Unit 	 27

Cameras, Optical 	 26

Cameras, Power Over Ethernet POE 	 37

Cameras, Power Over Ethernet POE 	 29

Cameras, Surveillance 	 24

Cameras, Thermal 	 26

Cameras, Unlimited Number of 	 122

Capability without Central Database, System 	 51

Capable Switch, Layer 3 	 37, 123

Capacity, Conduit Expansion 	 37

Capacity, DVMS 	 27

Capacity, Spare Cabinet 	 45

Capacity, Spare Enclosure 	 45

Capacity, Spare Input and Output 	 44

Capital Delivery Coordinator Department 	 12

Card Activities Access Granted Denied and Reason 	 12

Card Management Issues, Access 	 20

Card Reader Licences 	 11

Card Reader Pedestal 	 38

Card Reader Signals, Conditioning of 	 33

Card Reader, Arming Button 	 12

Card Reader, Disarming by 	 12

Card Reader, Elevator 	 30

Card Reader, Long Range 	 38, 118

Card Reader, Proximity 	 52

Card, Proximity 	 118

Category 6 Unshielded Twisted Pair UTP 	 123

Category 6 UTP 	 36

Catenary Supports 	 43

CCTV Image Lighting 	 25

CCTV Integration 	 7

CCTV Surveillance Commissioning 	 64

CCTV System Digital Video Management 	 9

CCTV, Closed Circuit Television System 	 123

Central Control Centre 	 7

Central Database, System Capability without 	 51

Central Monitoring Station 	 21

Centre, Architecture of Sites Connected to Main Regional Control 	 8

Centre, Central Control 	 7

Centre, Main Regional Control 	 7

Certification Test Results, Cable 	 53

Certification, Network Wiring 	 53

Certification, Virus and Malware Avoidance 	 9

Certified Barrier 	 111

Changes Approval by York Region 	 10

Changes by Authority Having Jurisdiction 	 10

Changes to Configuration, Minor 	 19

Charts, Addressing 	 9, 16, 17, 22

Checking Malware, Submittal Virus 	 15

Chemicals, Detection Loop Resistance to 	 40

CIF, Common Intermediate Format 	 25, 26

Circuit Television System CCTV, Closed 	 123

Circuit Television, Surveillance Closed 	 24

Circuit Working, Hot 	 42

Civil Electrical Communications Requirements for Parking Barrier 	 40

Clarifications 	 6

Clarifications, Technical 	 9

Class Size, Training 	 20

Clear Command, Panic 	 14

Client Application, Alarm Monitoring Software 	 13

Client, Alarm Monitoring Software 	 12

Close Out Documents 	 55

Closed Circuit Television System CCTV 	 123

Closed Circuit Television, Surveillance 	 24

CMP Rating, CMR or 	 37

CMR or CMP Rating 	 37

Code Compliant Washroom Kits 	 42

Code Exit Requirement, Elevator 	 31

Code OESC, Ontario Electrical Safety 	 37, 42, 124

Code Restrictions, Elevator 	 30

Code, Colour 	 134

CODEC, JPEG, MJPEG, H.264, H.265, Zipstream, Camera 	 28

Codes and Jurisdictions, Applicable 	 11

Codes Applicable to Security Projects, Standards, 	 77

Coding, Conduit Colour 	 124, 135

Colour and Black & White Images 	 26

Colour Code 	 134

Colour Coding, Conduit 	 124, 135

Colours, Convention for Conduit 	 125

Command, Panic Clear 	 14

Comment of Technical Shop Drawings, Review and 	 9

Comments and Concerns, Security System Installer 	 9

Commissioning Documentation 	 16

Commissioning Documentation, Detailed 	 17

Commissioning Form, Regional Approved 	 61

Commissioning Legend 	 61

Commissioning Minutes 	 19

Commissioning Schedule 	 16

Commissioning Scheduling 	 19

Commissioning Tests, Repetition of 	 19

Commissioning, CCTV Surveillance 	 64

Commissioning, Final 	 19

Commissioning, Testing and 	 10

Common Intermediate Format CIF 	 25, 26

Communication Cable Separation, Power 	 43

Communications Cabling, Shared Pathways for 	 34

Communications Line Extender 	 129

Communications Network Ports 	 47

Communications Network Warranty, Passive 	 54

Communications Protocols, Proprietary 	 47

Communications Requirements for Parking Barrier, Civil Electrical 	 40

Communications, 3rd Party Monitoring Station 	 49

Communications, Network 	 21

Communications, Off Site Monitoring Service Station 	 49

Compatibility with Announced Enhancements 	 28

Compatibility with Installation, Camera 	 28

Compatibility, Firmware Software Update 	 14

Compatible with Existing Installation 	 23

Complete Bill of Materials 	 16, 17, 22

Complete System, Verification of 	 53

Compliance with Specifications 	 10

Compliance, OBC 	 132

Compliant Washroom Kits, Code 	 42

Component Testing, Per System 	 18

Components, Access Control 	 112

Components, Cabinet 	 45

Components, Enclosure 	 45

Components, Intrusion Detection System 	 113

Components, Miscellaneous Contractor 	 46

Components, Panel 	 45

Components, Replacement 	 54

Components, Security Access Intrusion System 	 86

Components, Typical Security 	 82

Compound, Hazardous Area Seal Filling 	 124

Compression, Video 	 28

Concealed Magnetic Door Contacts 	 48

Conceptual Drawings 	 44

Concerns, Security System Installer Comments and 	 9

Condensation, Protection Against 	 45

Conditioning of Card Reader Signals 	 33

Conditioning, Air 	 9

Conductors and Miscellaneous Accessories, Cabling 	 126

Conduit Alignment, Raceway 	 43

Conduit Colour Coding 	 124, 135

Conduit Colours, Convention for 	 125

Conduit Expansion Capacity 	 37

Conduit Sealant 	 128

Conduit, Rigid PVC Schedule 40 	 124

Conduits 	 135

Conduits and Junction Boxes, Required 	 21

Conduits Fastenings and Fittings 	 124

Conduits Fittings and Accessories 	 124

Conduits or Cables, No Oversizing of 	 42

Conduits, Cabling Segregation in 	 21

Conduits, Pathways, Fittings, Cables, Accessories 	 37

Conduits, Rodent Sealing of 	 43

Confidentiality 	 6

Configurable Devices, Documentation of 	 18

Configuration Backup Files 	 17, 56

Configuration of Security System, Installation and 	 10

Configuration, Camera 	 27

Configuration, Minor Changes to 	 19

Configuration, Software System 	 11

Configuration, System Deployment and 	 12

Configurations, DIP Switch and Hardware 	 16, 21, 22

Configurations, Modifications to Existing 	 19

Configurations, Operational 	 56

Configurations, Standardised Security 	 23

Configurations, Standardised Security Door 	 82

Configurations, Temporary 	 56

Configure and Test, Program 	 12

Confirmation of Functionality 	 18

Confirmation of Functionality, Written 	 18

Confirmation of Security System Functions and Operation 	 50

Connected to Main Regional Control Centre, 
Architecture of Sites 	 8

Connection, TIA-568A Termination 	 36

Connections and Wiring Diagrams, Electrical 	 16, 17, 22

Connections, Electrical 	 9

Connectivity Diagrams, Network 	 9, 15, 21

Connectors, Optical 	 36

Connectors, Watertight Cable 	 43

Consequential Damages 	 24

Consistent Functionality Across Region 	 11

Construction Cylinders, Temporary 	 40

Construction Temporary Lock Cylinders 	 131

Construction Work, Execution of 	 42

Consultant Approval 	 56

Contact Information, Warranty 	 49, 134

Contacts for Alarm Points 	 49

Contacts, Concealed Magnetic Door 	 48

Contacts, Door 	 119

Contacts, Explosion Proof Door 	 119

Contacts, Intrinsically Safe Door 	 119

Contents, Table of 	 3

Continuous Video Recording 	 28

Continuous, Feeder Wiring 	 44

Contract Documents 	 6, 12, 15, 20, 44, 55, 110

Contract Price, Modifications to 	 11

Contract Termination 	 24

Contract, Breach of 	 24

Contractor Additional Parts 	 44

Contractor Assistance Requirement 	 19

Contractor Bill of Materials 	 44

Contractor Components, Miscellaneous 	 46

Contractor Identify Incompatibilities 	 44

Contractor Responsibility and Subcontractors 	 10

Contractor Responsibility for Errors 	 23

Contractor Spare Parts Recommendation 	 44

Contractor Staff Project Familiarity 	 20

Contractor Work, Unit Pricing of 	 46

Contractor, Door Hardware 	 10

Contractor, Fire Alarm System 	 47

Contractor, Pre Qualified Security System 	 10

Contractor, Routine Maintenance Training by 	 10

Contractor, Security Installation 	 15

Contractors, Electrical 	 10

Contractors, Network Installation 	 10

Contracts, Maintenance 	 17

Control and Intrusion Detection, Integration of Access 	 12

Control and Intrusion Detection, Security Access 	 23

Control and Parking Barrier, Integration of Access 	 39

Control Architecture, Elevator Access 	 31

Control Centre, Architecture of Sites Connected to Main Regional 	 8

Control Centre, Central 	 7

Control Centre, Main Regional 	 7

Control Components, Access 	 112

Control Detail, Door Type T5 Overhead 
Garage Door with Access 	 91

Control Devices, Parking 	 38

Control Elevator Fire Alarm, Access 	 31

Control Elevator Power Failure, Access 	 31

Control Equipment, Approved Access 	 114

Control Functions Arm Disarm Door Operations 	 14

Control Functions Intrusion Operations Map Navigation 	 14

Control Integration, Access 	 7

Control Integration, Elevator Access 	 30

Control Interface, Door Hardware 	 9

Control Interface, Dynamic Icons on Access 	 12

Control Intrusion Detection Integration, Access 	 9

Control of Barrier Arms, Access 	 38

Control Panel 	 14, 114, 116

Control Panel for ENV OMM, SCADA 	 13, 49

Control Panel Outputs, Waste and Wastewater 	 47

Control System Alarm Monitor, Access 	 13

Control System User Interface, Access 	 9

Control System Value Added Resellers, Access 	 110

Control System, Regional 	 7

Control Transformer 	 120

Control, Basic Elevator 	 30

Control, Bypass Switch for Elevator Access 	 34

Control, Fail Safe Elevator 	 33, 34

Control, Fail Secure Elevator 	 33, 34

Control, Limitations in Elevator Access 	 31, 34

Control, Multi Tenant Elevator Access 	 34

Control, Network Wiring Field Quality 	 53

Control, Parking 	 38

Control, Scheduling Elevator Access 	 34

Control, Security Wiring Field Quality 	 53

Control, Video Integration with Access 	 28

Controller, In Line Power 	 48

Controllers and Panels, System 	 60

Controllers, Adapters and 	 22

Convention for Conduit Colours 	 125

Convention Standards, Regional Security System Naming 	 14

Convention, Cable Labelling 	 136

Convention, Security System Naming 	 60

Conventions, Drawing 	 82

Coordination of Network Installation 	 21

Coordination with Region IT 	 12

Coordination, Network TCP/IP 	 21

Coordinator Department, Capital Delivery 	 12

Cords, Patch 	 54

Cost and Schedule Impact 	 10

Cost of Testing 	 12

Countdown Timer 	 52

Covert Imaging 	 26

CPTED, Crime Prevention Through Environmental Design 	 26

Crash Bar, Panic 	 40

Credential and Credential Reading Equipment, Approved 	 118

Credential Reading Equipment, Approved Credential and 	 118

Credential, Long Range Proximity Tag 	 118

Crime Prevention Through Environmental Design CPTED 	 26

Criteria for Detection Identification Recognition, Johnson's 	 25

Criteria, Image Search 	 29

Criteria, Lifetime Cabling Warranty 	 54

Criteria, Operating and Survival 	 109

Criteria, Performance 	 24

Criteria, Video Recording 	 28

Cumulative Down Time 	 55

Custom Alarms for Each Facility 	 13

Custom Alarms for Each Site 	 13

Custom Icons 	 14

Cut Sheets 	 9

Cut-Sheets, Product Specifications and 	 16, 17, 22

Cylinders, Construction Temporary Lock 	 131

Cylinders, Locks Keys and 	 131

Cylinders, Temporary Construction 	 40

D

Damages, Consequential 	 24

Data Interface FDDI, Fibre Distributed 	 36, 123

Data Sheets 	 16, 17

Data, Burn-In Image 	 29

Data, Performance 	 22

Database Integration, Application and 	 18

Database Programming 	 11

Database Server 	 21

Database Updates, Security System 	 11

Database, System Capability without Central 	 51

Databases, Repopulating System Related 	 19

Date and Time in ISO Format, Local 	 12

Deactivation, Schedule Activation and 	 12

Decommissioned Surplus Equipment 	 47

Defective Products Warranty 	 11

Defects, Report Existing 	 44

Deficiency Resolution 	 16

Definition, Standardised Security Terminology 	 65

Delay for Arming, Exit 	 12

Delay Time, Exit 	 13

Delay, Exit 	 52

Deliveries, Parking and 	 20

Delivery Coordinator Department, Capital 	 12

Demonstration to Region 	 18

Demonstration, Pre-Commissioning 	 19

Denied and Reason, Card Activities Access Granted 	 12

Department, Capital Delivery Coordinator 	 12

Departure Loop, Vehicle Parking 	 39

Deployment and Configuration, System 	 12

Description, Functional 	 22

Design CPTED, Crime Prevention Through Environmental 	 26

Design Evaluation 	 9

Design, Improvements to 	 6

Design, Technical 	 9

Destination Reporting, Elevator 	 31

Detail, Door Type T1 Arming Disarming Single Door 	 87

Detail, Door Type T2 Secondary Entrance Double Door 	 94

Detail, Door Type T2 Secondary Entrance Single Door 	 88

Detail, Door Type T3 Emergency Perimeter Exit Single 
Door 	 89

Detail, Door Type T4 Overhead Garage Door 	 90

Detail, Door Type T5 Overhead Garage Door with Access Control 	 91

Detail, Door Type T6 Pedestal for Gate Entrance 	 92

Detail, Door Type T7 Secondary Entry Single Door with Magnetic Lock 	 93

Detail, Door Type T8 Tamper Point Monitoring Point Installation 	 95

Detailed Commissioning Documentation 	 17

Details, Firmware 	 17

Details, Labelling 	 134

Details, Locksmith 	 41

Details, Warranty 	 16

Details, Wiring 	 22

Detection Arming, Intrusion 	 12

Detection Equipment, Approved Intrusion 	 116

Detection Identification Recognition, Johnson's Criteria for 	 25

Detection Integration, Access Control Intrusion 	 9

Detection Loop Amplifiers, Vehicle 	 40, 130

Detection Loop Resistance to Chemicals 	 40

Detection Loop, Activation, Entry and Reset Vehicle 	 39

Detection Loops, Vehicle 	 38, 40

Detection POD, Probability of 	 24

Detection Point Schedule, Intrusion 	 9, 16, 17, 22

Detection Point, Verification of Each 	 53

Detection System Components, Intrusion 	 113

Detection System Keypad Display, Intrusion 	 12

Detection System, Intrusion 	 7

Detection, Barrier Arm Interference 	 39

Detection, Door Open 	 12, 52

Detection, Image 	 25

Detection, Integration of Access Control and Intrusion 	 12

Detection, Intrusion 	 24

Detection, Security Access Control and Intrusion 	 23

Detector Loops, Vehicle 	 130

Detectors, Glass Break 	 120

Detectors, Motion 	 120

Deterrence Prevention, Intrusion 	 24

Device Functionality, Functional Tests for 	 53

Device Labelling 	 48

Device Landing Schedule 	 9, 16, 22

Device Legend, Security 	 62

Device Security Penetration IT, Network 	 11

Device Summary, Security System 	 85

Device Termination Diagrams, Typical and Site Specific 	 9

Device, Image Transmission to Mobile 	 29

Devices Panic Bars, Exit 	 119

Devices, Approved Network 	 12

Devices, Documentation of Configurable 	 18

Devices, Electro Magnetic Locking 	 47, 48

Devices, Individual Security 	 61

Devices, Industry Standard Recording 	 29

Devices, Installation, Security System 	 44

Devices, Miscellaneous Security 	 119

Devices, Parking Control 	 38

Devices, Pre-Approved 	 23, 24

Diagrams, Electrical Connections and Wiring 	 16, 17, 22

Diagrams, High Level Riser 	 9

Diagrams, Interconnection 	 23

Diagrams, Network Connectivity 	 9, 15, 21

Diagrams, System Integration Schematic(s) 
and Wiring 	 16, 17, 22

Diagrams, System Integration Wiring 	 9

Diagrams, System Riser 	 9, 15, 21

Diagrams, Tub Enclosure Layout 	 9, 16, 17, 22

Diagrams, Typical and Site Specific Device Termination 	 9

Diagrams, Typical and Site-Specific Termination/Wiring Schematic(s) and 	 16, 21

Diagrams, Vertical and Horizontal Wiring 	 9, 15, 21

Digital Cameras, Analogue, 	 27

Digital Image Signature 	 29

Digital Video Management System DVMS 	 24, 122, 123

Digital Video Management, CCTV System 	 9

DIN Rail Mounted Terminal Blocks 	 46

Diodes, Flyback 	 48

Diodes, Snubbing 	 48

DIP Switch and Hardware Configurations 	 16, 21, 22

DIP Switch Settings, Hardware 	 9

Direct Sunlight Impact on Camera Imaging 	 26

Disarm Door Operations, Control Functions Arm 	 14

Disarmed Normal Alarmed Forced Held Open, Status 
Armed 	 13, 14

Disarmed, Security System 	 52

Disarming by Card Reader 	 12

Disarming Single Door Detail, Door Type T1 Arming 	 87

Disarming, Failures Arming and 	 12

Dispatch Requirements, Elevator Passenger 	 33

Display, Intrusion Detection System Keypad 	 12

Disposition, Associated Status 	 13

Distinct Icons, Regional Facilities 	 13

Distributed Data Interface FDDI, Fibre 	 36, 123

Document Test and Verify 	 18

Documentation of Configurable Devices 	 18

Documentation Standards 	 81

Documentation Submissions 	 9, 81

Documentation, As-Built 	 16

Documentation, Commissioning 	 16

Documentation, Detailed Commissioning 	 17

Documentation, Hardware 	 22

Documentation, Integration Procedure 	 19

Documentation, Project 	 56

Documentation, System Operators 	 17

Documentation, Technical 	 15

Documents, Close Out 	 55

Documents, Contract 	 6, 12, 15, 20, 44, 55, 110

Documents, Reference 	 6

Door Configurations, Standardised Security 	 82

Door Contacts 	 119

Door Contacts, Concealed Magnetic 	 48

Door Contacts, Explosion Proof 	 119

Door Contacts, Intrinsically Safe 	 119

Door Detail, Door Type T1 Arming Disarming Single 	 87

Door Detail, Door Type T2 Secondary Entrance Double 	 94

Door Detail, Door Type T2 Secondary Entrance Single 	 88

Door Detail, Door Type T3 Emergency Perimeter Exit 
Single 	 89

Door Detail, Door Type T4 Overhead Garage 	 90

Door Hardware Contractor 	 10

Door Hardware Control Interface 	 9

Door Hardware, Locksmithing and 	 40

Door Held Open 	 50

Door Interface Relay 	 51

Door Locks 	 131

Door Names and Numbers 	 60

Door Open Detection 	 12, 52

Door Operations, Control Functions Arm Disarm 	 14

Door Operators ADO, Automatic 	 51

Door Reader, Perimeter 	 13

Door Release, Push Paddle 	 40, 131

Door Security Assemblies, Typical 	 82

Door Strikes, Electric 	 48, 119

Door Testing, Exterior Facility 	 57

Door Testing, Mechanical and Electronic 	 57

Door Type T1 Arming Disarming Single Door Detail 	 87

Door Type T2 Secondary Entrance Double Door Detail 	 94

Door Type T2 Secondary Entrance Single Door Detail 	 88

Door Type T3 Emergency Perimeter Exit Single Door 
Detail 	 89

Door Type T4 Overhead Garage Door Detail 	 90

Door Type T5 Overhead Garage Door with Access Control Detail 	 91

Door Type T6 Pedestal for Gate Entrance Detail 	 92

Door Type T7 Secondary Entry Single Door 
with Magnetic Lock Detail 	 93

Door Type T8 Tamper Point Monitoring Point 
Installation Detail 	 95

Door with Access Control Detail, Door Type T5 
Overhead Garage 	 91

Door with Magnetic Lock Detail, Door Type T7
 Secondary Entry Single 	 93

Door Forced 	 48, 50, 57

Double Door Detail, Door Type T2 Secondary Entrance 	 94

Down Time, Cumulative 	 55

Down Time, Penalties for 	 55

Drawing Conventions 	 82

Drawing Legend 	 82

Drawing Notes 	 83

Drawing Resubmission, Shop 	 23

Drawing Review, Shop 	 23

Drawing Title Block 	 82, 84

Drawing, Location 	 22

Drawings Prior to Execution 	 10

Drawings to Authority Having Jurisdiction, Working 	 10

Drawings, As-Built 	 56

Drawings, Assembly 	 23

Drawings, Conceptual 	 44

Drawings, Equipment Layout 	 22

Drawings, Review and Comment of Technical Shop 	 9

Drawings, Shop 	 21

Drawings, Technical Shop 	 9, 15

Dressing, Cable 	 54

Duct, Inner 	 36

Duration, Training 	 20

Duress Alarm 	 14

DVMS Capacity 	 27

DVMS Upgrades 	 28

DVMS, Digital Video Management System 	 24, 122, 123

Dynamic Icons 	 14

Dynamic Icons on Access Control Interface	 12

Dynamic Icons, Interface Map 	 13

E

Each Area, Verification of 	 53

Each Detection Point, Verification of 	 53

Each Facility, Custom Alarms for 	 13

Each Point, Verification of 	 53

Each Section, Verification of 	 53

Each Sensor, Verification of 	 53

Each Site, Custom Alarms for 	 13

Effectiveness, Security System 	 24

Electric Door Strikes 	 48, 119

Electric Strike Failure Modes 	 48

Electrical Communications Requirements for 
Parking Barrier, Civil 	 40

Electrical Connections 	 9

Electrical Connections and Wiring Diagrams 	 16, 17, 22

Electrical Contractors 	 10

Electrical Environmental Requirements, Physical 	 22

Electrical Installation 	 42

Electrical Insulating Tape 	 128

Electrical Power Transfer 	 119

Electrical Requirements 	 9

Electrical Safety Authority ESA 	 42

Electrical Safety Code OESC, Ontario 	 37, 42, 124

Electro Magnetic Locking Devices 	 47, 48

Electronic Door Testing, Mechanical and 	 57

Elevator Access Control Architecture 	 31

Elevator Access Control Integration 	 30

Elevator Access Control, Bypass Switch for 	 34

Elevator Access Control, Limitations in 	 31, 34

Elevator Access Control, Multi Tenant 	 34

Elevator Access Control, Scheduling 	 34

Elevator Card Reader 	 30

Elevator Code Exit Requirement 	 31

Elevator Code Restrictions 	 30

Elevator Control, Basic 	 30

Elevator Control, Fail Safe 	 33, 34

Elevator Control, Fail Secure 	 33, 34

Elevator Destination Reporting 	 31

Elevator Fire Alarm, Access Control 	 31

Elevator Fire Recall 	 31, 34

Elevator Floor Button 	 30

Elevator High Level Integration HLI 	 31

Elevator Integration Limitations 	 30

Elevator Passenger Dispatch Requirements 	 33

Elevator Power Failure, Access Control 	 31

Elevator Service Mode 	 33

Elevator Travelling Cable 	 31, 33

Elevators, Access Levels for 	 34

E-Mail, Image Forwarding to 	 29

Emergency Button Alarms 	 42

Emergency Mechanical Key Override 	 57

Emergency Perimeter Exit Single Door Detail, Door 
Type T3 	 89

EMF, Suppression of Induced Back 	 48

Emulation Software, Camera 	 27

Enclosure Capacity, Spare 	 45

Enclosure Components 	 45

Enclosure Labelling 	 48

Enclosure Layout Diagrams, Tub 	 9, 16, 17, 22

Enclosure Solutions 	 45

Enclosure Specifications 	 44

Enclosure Tamper 	 14

Enclosure Ventilation 	 45

Enclosures 	 134

Enclosures, Fibre Optic 	 36

Encoders, Camera 	 27

Encoding, NTSC PAL 	 27

End Equipment Installation, Head 	 10

End Of Line EOL Supervision 	 46

English, Training in 	 20

Engraved Lamacoid 	 133

Enhancements, Compatibility with Announced 	 28

Enterprise Software Integration, Installation 	 50

Entire Site, Audit Trail Log for 	 12, 13

Entire System Testing, Per Total 	 18

Entrance Detail, Door Type T6 Pedestal for Gate 	 92

Entrance Double Door Detail, Door Type T2 Secondary 	 94

Entrance Single Door Detail, Door Type T2 Secondary 	 88

Entry and Reset Vehicle Detection Loop, Activation, 	 39

Entry Single Door with Magnetic Lock Detail, 
Door Type T7 Secondary 	 93

ENV OMM, SCADA Control Panel for 	 13, 49

Environmental Design CPTED, Crime Prevention Through 	 26

Environmental Requirements 	 109

Environmental Requirements, Parking Barrier 	 40

Environmental Requirements, Physical Electrical 	 22

EOL Supervision, End Of Line 	 46

Equipment Acquisition 	 6

Equipment Installation, Head End 	 10

Equipment Layout Drawings 	 22

Equipment Licencing Hardware, System 	 10

Equipment Literature 	 22

Equipment Location, Relocation of 	 45

Equipment Substitution Approval 	 24

Equipment Substitution Procedure 	 96

Equipment Substitution Products 	 98

Equipment Substitution Quality Assurance 	 98

Equipment, Approved Access Control 	 114

Equipment, Approved Credential and Credential Reading 	 118

Equipment, Approved Intercom 	 117

Equipment, Approved Intrusion Detection 	 116

Equipment, Decommissioned Surplus 	 47

Equipment, Labelling of All 	 133

Equipment, List of Approved Security 	 111

Equipment, Pre-Approved 	 111

Equipment, Relocation of 	 46

Errors, Contractor Responsibility for 	 23

ESA, Electrical Safety Authority 	 42

Escalation Resolution, Problem 	 20

Ethernet POE Cameras, Power Over 	 37

Ethernet POE POE Cameras, Power Over 	 29

Ethernet, 1000Base-LX Gigabit 	 123

Ethernet, 1000Base-SX Gigabit 	 123

Ethernet, 1000Base-TX Gigabit 	 123

Ethernet, 1000BaseTX Gigabit 	 34, 36

Evaluation, Design 	 9

Evaluation, Training Program 	 21

Evidence Lock, Image 	 29

Examples of Cable Labelling 	 137, 138

Execution of Construction Work 	 42

Execution, Drawings Prior to 	 10

Existing Buildings 	 60

Existing Configurations, Modifications to 	 19

Existing Defects, Report 	 44

Existing Installation, Compatible with 	 23

Existing System, Integration of Facility into 	 50

Exit RTE Function, Request to 	 50

Exit Delay 	 52

Exit Delay for Arming 	 12

Exit Delay Time 	 13

Exit Devices Panic Bars 	 119

Exit Push Buttons 	 120

Exit Requirement, Elevator Code 	 31

Exit Sensors RTE REX, Request to 	 120

Exit Single Door Detail, Door Type T3 Emergency 
Perimeter 	 89

Expansion Capacity, Conduit 	 37

Expert Advice 	 20

Explanation of the Sequence of Operation 	 16, 17, 22

Explosion Proof 	 111

Explosion Proof Door Contacts 	 119

Extender, Communications Line 	 129

Exterior Antenna 	 21

Exterior Facility Door Testing 	 57

Eyes, Pulling 	 42

F

Facial Recognition 	 29

Facilities Distinct Icons, Regional 	 13

Facility Door Testing, Exterior 	 57

Facility into Existing System, Integration of 	 50

Facility Wide Alarm 	 57

Facility, Custom Alarms for Each 	 13

Facility, Real Time Status of 	 14

Factory Trained Installers 	 6

Factory Trained Technicians 	 6

Fail Battery Trouble, Status Offline AC 	 14

Fail Over, Redundancy and 	 28

Fail Safe Elevator Control 	 33, 34

Fail Secure Elevator Control 	 33, 34

Fail, Power Failure, AC Restore, Power Restore, AC 	 14

Failure Mode, Parking Barrier Power 	 39

Failure Modes, Electric Strike 	 48

Failure Operation, Power 	 51

Failure, AC Restore, Power Restore, AC Fail, Power 	 14

Failure, Access Control Elevator Power 	 31

Failure, System 	 55

Failures Arming and Disarming 	 12

Faithful and Reliable Recordings 	 28

False Alarm 	 24

False Alarm Rate FAR 	 24

Familiarity, Contractor Staff Project 	 20

FAR, False Alarm Rate 	 24

Fastenings and Fittings, Conduits 	 124

Fault, Inhibit Arming on 	 57

Faulted Active On Schedule, Status Unlocked Tamper 	 14

FDDI, Fibre Distributed Data Interface 	 36, 123

Features, Available 	 17

Feeder Wiring Continuous 	 44

Fibre Backbone Requirement 	 36

Fibre Distributed Data Interface FDDI 	 36, 123

Fibre Optic Enclosures 	 36

Fibre, Optical 	 123

Field Locations 	 10

Field Quality Control, Network Wiring 	 53

Field Quality Control, Security Wiring 	 53

Field Tag Numbers 	 22

Field Wiring Terminations 	 128

Files, CAD PDF Source 	 13

Files, Configuration Backup 	 17, 56

Filling Compound, Hazardous Area Seal 	 124

Final Acceptance Testing 	 18

Final Commissioning 	 19

Final Submittal Review Arbiter 	 15

FIPPA Privacy Regulations 	 29

Fire Alarm System Contractor 	 47

Fire Alarm, Access Control Elevator 	 31

Fire Recall, Elevator 	 31, 34

Fire Sealant 	 129

Fire Separation, Maintain 	 43

Firmware 	 23

Firmware Approval, Upgrade Camera 	 28

Firmware Details 	 17

Firmware Software Update Compatibility 	 14

Firmware Version 	 16

Firmware Versions, Software and 	 23

Fittings and Accessories, Conduits 	 124

Fittings, Cables, Accessories, Conduits, Pathways, 	 37

Fittings, Conduits Fastenings and 	 124

Fixed Lens Cameras 	 27, 28

Flame Test Rating 	 46

Flash Precautions, Arc 	 42

Flexible Cable Labels 	 133

Floor Access, Locked 	 31

Floor Button, Elevator 	 30

Floor Plan, Architectural 	 13

Floorplan, System Layout 	 15, 21

Flyback Diodes 	 48

Force Sensors HFS, Hold 	 47

Forced Held Open Locked, Status Normal Alarmed 	 14

Forced Held Open, Status Armed Disarmed Normal 
Alarmed 	 13, 14

Form, Regional Approved Commissioning 	 61

Form, Substitution Request 	 100

Format and Style, Submittal 	 15

Format CIF, Common Intermediate 	 25, 26

Format, Image 	 28

Format, Local Date and Time in ISO 	 12

Forwarding to E-Mail, Image 	 29

Frame Rate 	 25, 26

Free Washroom, Barrier 	 41

FT-4 or FT-6 Rating 	 37

FT-6 Rating, FT-4 or 	 37

Function Basis Testing, Per 	 18

Function, Request to Exit RTE 	 50

Functional Description 	 22

Functional Tests for Device Functionality 	 53

Functionality Across Region, Consistent 	 11

Functionality, Confirmation of 	 18

Functionality, Functional Tests for Device 	 53

Functionality, Written Confirmation of 	 18

Functions and Operation, Confirmation of Security System 	 50

Functions Arm Disarm Door Operations, Control 	 14

Functions Intrusion Operations Map Navigation, Control 	 14

Functions, Administrative 	 17

G

Garage Door Detail, Door Type T4 Overhead 	 90

Garage Door with Access Control Detail, Door Type T5 Overhead 	 91

Gate Access 	 7

Gate Entrance Detail, Door Type T6 Pedestal for 	 92

Gate Manufacturer 	 38

General Overview 	 50

General Requirements 	 6

General, Operation 	 50

Gigabit Ethernet, 1000Base-LX 	 123

Gigabit Ethernet, 1000Base-SX 	 123

Gigabit Ethernet, 1000Base-TX 	 123

Gigabit Ethernet, 1000BaseTX 	 34, 36

Glass Break Detectors 	 120

Granted Denied and Reason, Card Activities Access 	 12

Granted, Access 	 52

Graphic Alarm Map, Sample 	 139

Graphic Map, Image Resolution of 	 13, 25

Graphical Map, Update 	 13

Graphical User Interface 	 13

Grips, Cable 	 42, 43, 128

Ground, Telecommunications 	 48

Grounding Requirements 	 48

H

H.264, H.265, Zipstream, Camera CODEC, JPEG, MJPEG, 	 28

H.265, Zipstream, Camera CODEC, JPEG, MJPEG, H.264, 	 28

Handicapped Operator Requirements 	 51

Hardening 	 24

Hardware Configurations, DIP Switch and 	 16, 21, 22

Hardware Contractor, Door 	 10

Hardware Control Interface, Door 	 9

Hardware DIP Switch Settings 	 9

Hardware Documentation 	 22

Hardware Modules and Points, Addresses for 	 23

Hardware, Locksmithing and Door 	 40

Hardware, Programmable 	 22

Hardware, System Equipment Licencing 	 10

Having Jurisdiction, Changes by Authority 	 10

Having Jurisdiction, Working Drawings to Authority 	 10

Hazardous Locations 	 111

Hazardous Area Seal Filling Compound 	 124

Head End Equipment Installation 	 10

Headroom for Cable Installation 	 43

Health Services 	 7

Held Open Locked, Status Normal Alarmed Forced 	 14

Held Open, Door 	 50

Held Open, Status Armed Disarmed Normal Alarmed 
Forced 	 13, 14

HFS, Bond Sensors 	 47

HFS, Hold Force Sensors 	 47

Hierarchy, Multilayer 	 13

High Level Integration HLI, Elevator 	 31

High Level Riser Diagrams 	 9

History, Revision 	 2

HLI, Elevator High Level Integration 	 31

Hold Force Sensors HFS 	 47

Horizontal Wiring Diagrams, Vertical and 	 9, 15, 21

Hot Circuit Working 	 42

Humidity, Operating 	 109

I

Icons on Access Control Interface, Dynamic 	 12

Icons, Custom 	 14

Icons, Dynamic 	 14

Icons, Interface Map Dynamic 	 13

Icons, Regional Facilities Distinct 	 13

Icons, Sample Regional Layout and 	 139

Identification Labels 	 134

Identification Recognition, Johnson's Criteria for Detection 	 25

Identification, Image 	 25

Identification, Wiring 	 56

Identifier PIN Assignment, Location 	 22

Identify Incompatibilities, Contractor 	 44

Illumination and Shadows 	 26

Illumination Lighting Sources 	 27

Illumination, Barrier Arm 	 38

Illuminator, Infra Red 	 26

Image Archiving, Video 	 29

Image Data, Burn-In 	 29

Image Detection 	 25

Image Evidence Lock 	 29

Image Format 	 28

Image Forwarding to E-Mail 	 29

Image Identification 	 25

Image Lighting, CCTV 	 25

Image Quality Affected by Vibration 	 25

Image Recognition 	 25

Image Recording, Privacy Laws Regarding 	 29

Image Resolution 	 25

Image Resolution of Graphic Map 	 13, 25

Image Search Bookmarking 	 29

Image Search Criteria 	 29

Image Signature, Digital 	 29

Image Transmission to Mobile Device 	 29

Images, Colour and Black & White 	 26

Images, Shaky 	 25

Imaging, Covert 	 26

Imaging, Direct Sunlight Impact on Camera 	 26

Impact on Camera Imaging, Direct Sunlight 	 26

Impact, Cost and Schedule 	 10

Implementation Plan Approval 	 11

Improvements to Design 	 6

Improvements to Specifications 	 6

In and Out, Operator Logging 	 12

In Line Power Controller 	 48

Incident Repair Times, Monthly 	 55

Incident Response Times 	 55

Incident, Recording Prior to 	 28

Incompatibilities, Contractor Identify 	 44

Independent Systems 	 7

Indicator, Armed LED 	 52

Individual Security Devices 	 61

Induced Back EMF, Suppression of 	 48

Industry Standard Recording Devices 	 29

Information Required for the Installation, Relevant 	 16, 17, 22

Information Technology Services 	 12, 21

Information Technology, Meet All Regional Standards Security, Operational, 	 11

Information, Warranty Contact 	 49, 134

Infra Red Cameras 	 26

Infra Red Illuminator 	 26

Infrastructure, Additional 	 21

Inhibit Arming on Fault 	 57

Injectors, Power 	 37

Inner Duct 	 36

Input and Output Capacity, Spare 	 44

Input Output Modules 	 114, 116

Installation and Configuration of Security System 	 10

Installation Contractor, Security 	 15

Installation Contractors, Network 	 10

Installation Detail, Door Type T8 Tamper Point 
Monitoring Point 	 95

Installation Enterprise Software Integration 	 50

Installation Manuals 	 17

Installation of Wires and Cables 	 42

Installation Recommendations, Manufacturer's 	 45

Installation Software 	 56

Installation, Camera Compatibility with 	 28

Installation, Compatible with Existing 	 23

Installation, Coordination of Network 	 21

Installation, Electrical 	 42

Installation, Head End Equipment 	 10

Installation, Headroom for Cable 	 43

Installation, Relevant Information Required for the 	 16, 17, 22

Installation, Security System Devices 	 44

Installation, Transformer 	 47

Installer Comments and Concerns, Security System 	 9

Installer, Security System 	 10

Installers, Factory Trained 	 6

Installers, Pre Qualified Value Added Resellers and 	 11

Instant Alarm 	 13

Insulating Tape, Electrical 	 128

Integrated Security System 	 7

Integration HLI, Elevator High Level 	 31

Integration Licences, Proprietary 	 11

Integration Limitations, Elevator 	 30

Integration of Access Control and Intrusion Detection 	 12

Integration of Access Control and Parking Barrier 	 39

Integration of Facility into Existing System 	 50

Integration Procedure Documentation 	 19

Integration Schematic(s) and Wiring Diagrams, 
System 	 16, 17, 22

Integration Techniques and Operational Scenarios 	 16, 17, 22

Integration Wiring Diagrams, System 	 9

Integration with Access Control, Video 	 28

Integration with Phone System, Intercom 	 8

Integration, Access Control 	 7

Integration, Access Control Intrusion Detection 	 9

Integration, Application and Database 	 18

Integration, CCTV 	 7

Integration, Elevator Access Control 	 30

Integration, Installation Enterprise Software 	 50

Integration, Intercom 	 7

Interactive Map 	 12

Intercom 	 38

Intercom Equipment, Approved 	 117

Intercom Integration 	 7

Intercom Integration with Phone System 	 8

Interconnection Diagrams 	 23

Interconnection, Backbone 	 36

Interface FDDI, Fibre Distributed Data 	 36, 123

Interface Map Dynamic Icons 	 13

Interface Relay 	 51

Interface Relay, Door 	 51

Interface Unit, Reader 	 114

Interface, Access Control System User 	 9

Interface, Door Hardware Control 	 9

Interface, Graphical User 	 13

Interface, Single User 	 7

Interface, Dynamic Icons on Access Control 	 12

Interference Detection, Barrier Arm 	 39

Intermediate Format CIF, Common 	 25, 26

Internal Standards 	 77

International Standards 	 77

Intrinsically Safe 	 111

Intrinsically Safe Door Contacts 	 119

Introduction 	 6

Intruder, Target 	 25

Intrusion Alarm 	 53

Intrusion Detection 	 24

Intrusion Detection Arming 	 12

Intrusion Detection Equipment, Approved 	 116

Intrusion Detection Integration, Access Control 	 9

Intrusion Detection Point Schedule 	 9, 16, 17, 22

Intrusion Detection System 	 7

Intrusion Detection System Components 	 113

Intrusion Detection System Keypad Display 	 12

Intrusion Detection, Integration of Access Control and 	 12

Intrusion Detection, Security Access Control and 	 23

Intrusion Deterrence Prevention 	 24

Intrusion Operations Map Navigation, Control Functions 	 14

Intrusion System Components, Security Access 	 86

Investigation, Security Staff 	 24

IP Address Requirements 	 47

ISO Format, Local Date and Time in 	 12

Issues, Access Card Management 	 20

IT Requirements, Server Network Other 	 12

IT, Coordination with Region 	 12

IT, Network Device Security Penetration 	 11

ITS Cable and Wiring Standard, York 	 34

J

Johnson's Criteria for Detection Identification Recognition 	 25

JPEG, MJPEG, H.264, H.265, Zipstream, Camera CODEC, 	 28

Judicial Services 	 7

Jumpers and Switches 	 23

Junction Boxes, Required Conduits and 	 21

Jurisdiction, Changes by Authority Having 	 10

Jurisdiction, Working Drawings to Authority Having 	 10

Jurisdictions, Applicable Codes and 	 11

K

Key Override, Emergency Mechanical 	 57

Key, Manual Override 	 53

Keypad 	 116

Keypad Display, Intrusion Detection System 	 12

Keypads, Alarm Annunciation on All 	 13

Keypads, Annunciator Alarm 	 13

Keys 	 56

Keys and Cylinders, Locks 	 131

Keys, Master 	 41

Keys, Medeco Override 	 46

Keys, Pass 	 41

Keyword List 	 56

Keywords 	 17

Kit, Available Washroom 	 132

Kits, Code Compliant Washroom 	 42

L

Labelling Convention, Cable 	 136

Labelling Details 	 134

Labelling of All Equipment 	 133

Labelling Requirements 	 56

Labelling Standard, Adherence to 	 136, 137

Labelling, Battery 	 14

Labelling, Cabinet 	 48

Labelling, Cable 	 135

Labelling, Device 	 48

Labelling, Enclosure 	 48

Labelling, Examples of Cable 	 137, 138

Labelling, Wiring 	 56

Labels, Flexible Cable 	 133

Labels, Identification 	 134

Labels, Warning 	 134

Labels, Wire and Cable Markers 	 128

Lamacoid, Engraved 	 133

LAN for Security Applications 	 34, 37

LAN VLAN, Virtual 	 37

LAN, Local Area Network 	 36, 123

Landing Schedule, Device 	 9, 16, 22

Language 	 15

Laws Regarding Image Recording, Privacy 	 29

Layer 3 Capable Switch 	 37, 123

Layout and Icons, Sample Regional 	 139

Layout Diagrams, Tub Enclosure 	 9, 16, 17, 22

Layout Drawings, Equipment 	 22

Layout Floorplan, System 	 15, 21

Lead Acid Batteries, Rechargeable 	 119

LED Indicator, Armed 	 52

Legend, Commissioning 	 61

Legend, Drawing 	 82

Legend, Security Device 	 62

Length, Cable Pulling 	 43

Lens Cameras, Fixed 	 27, 28

Level Integration HLI, Elevator High 	 31

Level Requirements, Service 	 55

Level Riser Diagrams, High 	 9

Levels for Elevators, Access 	 34

Levels, Access 	 14

Levels, Local Access 	 52

Levels, Regional Access 	 52

Levels, Target Service 	 54

Licence Assignment 	 56

Licence Plate Recognition LPR North America 	 30

Licences 	 17

Licences, Card Reader 	 11

Licences, Proprietary Integration 	 11

Licences, Workstation 	 11

Licencing Hardware, System Equipment 	 10

Licencing, Software 	 11

Life Safety Alarms 	 7

Lifetime Cabling Warranty Criteria 	 54

Light Cameras, Low 	 26

Lighting Sources, Illumination 	 27

Lighting Upgrades 	 29

Lighting, CCTV Image 	 25

Limitations in Elevator Access Control 	 31, 34

Limitations, Elevator Integration 	 30

Line Extender, Communications 	 129

Line Power Controller, In 	 48

List of Approved Security Equipment 	 111

List, Appendix 	 59

List, Keyword 	 56

List, Password 	 17, 56

List, Wiring 	 46

Listing, Site 	 60

Listings, Programming 	 23

Literature, Equipment 	 22

Live System 	 21

Local Access Levels 	 52

Local Alarms 	 57

Local Date and Time in ISO Format 	 12

Local Security Operation 	 7, 8

Local Area Network LAN 	 36, 123

Location Drawing 	 22

Location Identifier PIN Assignment 	 22

Location, Relocation of Equipment 	 45

Location, Training 	 20

Locations and Sites 	 12

Locations, Field 	 10

Locations, Hazardous 	 111

Locations, Splice 	 44, 46

Lock Cylinders, Construction Temporary 	 131

Lock Detail, Door Type T7 Secondary Entry 
Single Door with Magnetic 	 93

Lock, Image Evidence 	 29

Locked Floor Access 	 31

Locked, Status Normal Alarmed Forced Held Open 	 14

Locking Devices, Electro Magnetic 	 47, 48

Locks Keys and Cylinders 	 131

Locks, Door 	 131

Locksmith Details 	 41

Locksmith Subcontractors 	 10

Locksmithing and Door Hardware 	 40

Log for Entire Site, Audit Trail 	 12, 13

Log Verification, Audit Trail 	 57

Logging In and Out, Operator 	 12

Logging, Parking Barrier Activity 	 39

Long Range Card Reader 	 38, 118

Long Range Proximity Tag Credential 	 118

Loop Amplifiers, Vehicle Detection 	 40, 130

Loop Resistance to Chemicals, Detection 	 40

Loop, Activation, Entry and Reset Vehicle Detection 	 39

Loop, Vehicle Parking Departure 	 39

Loops, Vehicle Detection 	 38, 40

Loops, Vehicle Detector 	 130

Low Light Cameras 	 26

LPR North America, Licence Plate Recognition 	 30

Lubricant, Cable Pulling 	 43, 128

M

Made Aware 	 55

Magnetic Door Contacts, Concealed 	 48

Magnetic Lock Detail, Door Type T7 Secondary Entry 
Single Door with 	 93

Magnetic Locking Devices, Electro 	 47, 48

Main Regional Control Centre 	 7

Main Regional Control Centre, Architecture of Sites 
Connected to 	 8

Maintain Fire Separation 	 43

Maintenance Contracts 	 17

Maintenance Manuals 	 17

Maintenance Requirements Schedule 	 17

Maintenance Requirements, Backup and 	 23

Maintenance Training 	 19

Maintenance Training by Contractor, Routine 	 10

Malware Avoidance Certification, Virus and 	 9

Malware, Submittal Virus Checking 	 15

Management Issues, Access Card 	 20

Management System DVMS, Digital Video 	 122, 123

Management, CCTV System Digital Video 	 9

Management, Visitor 	 20

Manual Operation, Parking Barrier 	 39

Manual Override Key 	 53

Manuals, Installation 	 17

Manuals, Maintenance 	 17

Manuals, System Administration 	 17

Manuals, Technical 	 17

Manuals, User 	 56

Manufacturer Supplied Applications 	 12

Manufacturer, Gate 	 38

Manufacturer's Installation Recommendations 	 45

Map Dynamic Icons, Interface 	 13

Map Navigation, Control Functions Intrusion Operations 	 14

Map, Image Resolution of Graphic 	 13, 25

Map, Interactive 	 12

Map, Sample Graphic Alarm 	 139

Map, Update Graphical 	 13

Markers Labels, Wire and Cable 	 128

Markers, Cable 	 43

Master Keys 	 41

Materials BOM, Bill of 	 22

Materials, Complete Bill of 	 16, 17, 22

Materials, Contractor Bill of 	 44

Materials, Training Reference 	 20

Mechanical and Electronic Door Testing 	 57

Mechanical Key Override, Emergency 	 57

Medeco Override Keys 	 46

Meet All Regional Standards Security, Operational, 
Information Technology 	 11

Messengers, Cable 	 43

MFIPPA Privacy Regulations 	 29

Minor Changes to Configuration 	 19

Minutes, Commissioning 	 19

Miscellaneous Accessories, Cabling Conductors and 	 126

Miscellaneous Accessories, Wiring and 	 126

Miscellaneous Contractor Components 	 46

Miscellaneous Security Devices 	 119

MJPEG, H.264, H.265, Zipstream, Camera CODEC, JPEG, 	 28

Mobile Device, Image Transmission to 	 29

Mode ATM, Asynchronous Transfer 	 36

Mode, Elevator Service 	 33

Mode, Parking Barrier Power Failure 	 39

Modelling Software, Camera 	 27

Modem and Network Switch, Wireless 	 21, 47

Modes, Electric Strike Failure 	 48

Modifications to Contract Price 	 11

Modifications to Existing Configurations 	 19

Modifications, Allowed 	 11

Module Assignment, Rack 	 22

Module Tag Assignments 	 22

Modules and Points, Addresses for Hardware 	 23

Modules, Input Output 	 114, 116

Moisture and Waterproofing 	 128

Monitor Zones 	 14

Monitor, Access Control System Alarm 	 13

Monitored Off-Site, Alarm Types to be 	 49

Monitoring Point Installation Detail, Door Type T8 
Tamper Point 	 95

Monitoring Service Station Communications, Off Site 	 49

Monitoring Service Station, Off Site 	 13, 42

Monitoring Software Client Application, Alarm 	 13

Monitoring Software Client, Alarm 	 12

Monitoring Station Communications, 3rd Party 	 49

Monitoring Station Notification, Testing 	 50

Monitoring Station, Central 	 21

Monitoring, Alarm 	 7

Monitoring, Remote 	 14

Monitoring, Universal Washroom Alarm 	 42

Monthly Incident Repair Times 	 55

Motion Detectors 	 120

Motion, Video Recording on 	 28

Mounted Terminal Blocks, DIN Rail 	 46

Multi Technology Reader 	 118

Multi Tenant Elevator Access Control 	 34

Multi Unit Cameras 	 27

Multilayer Hierarchy 	 13

Multi-Mode Cable OM4, Optical 	 36

Municipal Boundaries 	 13

Municipal Standards 	 77

N

Name, Unique 	 60

Names and Numbers, Door 	 60

Naming Convention Standards, Regional Security System 	 14

Naming Convention, Security System 	 60

Naming of Alarm Points 	 49

National Standards 	 77

Navigation, Control Functions Intrusion Operations Map 	 14

Network and Video Cabling 	 34, 123

Network Cable Warranty 	 54

Network Communications 	 21

Network Connectivity Diagrams 	 9, 15, 21

Network Device Security Penetration IT 	 11

Network Devices, Approved 	 12

Network Installation Contractors 	 10

Network Installation, Coordination of 	 21

Network LAN, Local Area 	 36, 123

Network Other IT Requirements, Server 	 12

Network Penetration Requirements 	 21

Network Ports, Communications 	 47

Network Switch, Wireless Modem and 	 21, 47

Network Switches 	 12

Network TCP/IP Coordination 	 21

Network Video Recorders NVR 	 29

Network WAN, Wide Area 	 21

Network Warranty, Passive Communications 	 54

Network Wiring Certification 	 53

Network Wiring Field Quality Control 	 53

No Oversizing of Conduits or Cables 	 42

Normal Alarmed Forced Held Open Locked, Status 	 14

Normal Alarmed Forced Held Open, Status Armed 
Disarmed 	 13, 14

North America, Licence Plate Recognition LPR 	 30

Notes, Drawing 	 83

Notes, Technical 	 17

Notice to Proceed 	 15

Notification Verification, 3rd Party 	 57

Notification, Testing Monitoring Station 	 50

Notification, Wireless Alarm 	 49

NTSC PAL Encoding 	 27

Nuisance Alarm 	 24

Number of Cameras, Unlimited 	 122

Numbers, Door Names and 	 60

Numbers, Field Tag 	 22

Numbers, Serial 	 17, 56

Numbers, Terminal 	 22

Numbers, Wire 	 22

NVR, Network Video Recorders 	 29

O

OBC Compliance 	 132

Objectives, Security System 	 24

OESC, Ontario Electrical Safety Code 	 37, 42, 124

Off Site Monitoring Service Station 	 13, 42

Off Site Monitoring Service Station Communications 	 49

Offline AC Fail Battery Trouble, Status 	 14

Offline Operation, Seamless 	 9

Off-Site, Alarm Types to be Monitored 	 49

OM4, Optical Multi-Mode Cable 	 36

OMM, SCADA Control Panel for ENV 	 13, 49

On Schedule, Status Unlocked Tamper Faulted Active 	 14

Ontario Electrical Safety Code OESC 	 37, 42, 124

Open Detection, Door 	 12, 52

Operating and Survival Criteria 	 109

Operating Humidity 	 109

Operating Temperature 	 109

Operation ADO, Sequence of 	 51

Operation General 	 50

Operation Training, Routine 	 19

Operation, Anti Passback Parking 	 39

Operation, Confirmation of Security System Functions and 	 50

Operation, Explanation of the Sequence of 	 16, 17, 22

Operation, Local Security 	 7, 8

Operation, Parking Barrier Manual 	 39

Operation, Power Failure 	 51

Operation, Seamless Offline 	 9

Operation, Stand Alone 	 51

Operation, Theory of 	 17

Operational Configurations 	 56

Operational Scenarios, Integration Techniques and 	 16, 17, 22

Operational Sequencing 	 53

Operational, Information Technology, Meet All Regional Standards Security, 	 11

Operations Map Navigation, Control Functions Intrusion 	 14

Operations, Control Functions Arm Disarm Door 	 14

Operator Logging In and Out 	 12

Operator Requirements, Handicapped 	 51

Operators ADO, Automatic Door 	 51

Operators Documentation, System 	 17

Operators, System 	 7

Optic Enclosures, Fibre 	 36

Optical Cameras 	 26

Optical Connectors 	 36

Optical Fibre 	 123

Optical Multi-Mode Cable OM4 	 36

Optimal Performance 	 18

Other IT Requirements, Server Network 	 12

Out, Operator Logging In and 	 12

Output Capacity, Spare Input and 	 44

Output Modules, Input 	 114, 116

Outputs, Waste and Wastewater Control Panel 	 47

Over Ethernet POE Cameras, Power 	 37

Over Ethernet POE POE Cameras, Power 	 29

Over, Redundancy and Fail 	 28

Overall Project Summary 	 61

Overall System Availability 	 54

Overhead Garage Door Detail, Door Type T4 	 90

Overhead Garage Door with Access Control Detail, 
Door Type T5 	 91

Override Key, Manual 	 53

Override Keys, Medeco 	 46

Override, Emergency Mechanical Key 	 57

Oversizing of Conduits or Cables, No 	 42

Overview of Specifications 	 7

Overview, General 	 50

P

Pac, Smart 	 48

Paddle Door Release, Push 	 40, 131

Pair UTP, Category 6 Unshielded Twisted 	 123

Pair UTP, Unshielded Twisted 	 36

PAL Encoding, NTSC 	 27

Pan Tilt and Zoom PTZ Camera 	 27, 123

Panel Components 	 45

Panel for ENV OMM, SCADA Control 	 13, 49

Panel Outputs, Waste and Wastewater Control 	 47

Panel Solutions, Cabinet, 	 45

Panel Ventilation, Cabinet, 	 45

Panel, Control 	 14, 114, 116

Panel, Status 	 14

Panels, Patch 	 54

Panels, System Controllers and 	 60

Panic Alarm 	 7, 14, 42

Panic Bars, Exit Devices 	 119

Panic Clear Command 	 14

Panic Crash Bar 	 40

Parking and Deliveries 	 20

Parking Barrier Arm, Breakaway 	 39

Parking Barrier Arms 	 130

Parking Barrier, Cameras at 	 38

Parking Barrier, Civil Electrical Communications 
Requirements for 	 40

Parking Barrier, Integration of Access Control and 	 39

Parking Barrier, Physical Protection of 	 40

Parking Barriers 	 130

Parking Control 	 38

Parking Control Devices 	 38

Parking Departure Loop, Vehicle 	 39

Parking Operation, Anti Passback 	 39

Parking Barrier Activity Logging 	 39

Parking Barrier Environmental Requirements 	 40

Parking Barrier Manual Operation 	 39

Parking Barrier Power Failure Mode 	 39

Participation in Testing, Region 	 57

Parts Recommendation, Contractor Spare 	 44

Parts, Contractor Additional 	 44

Parts, Replacement Spare 	 18

Parts, Spare 	 56

Party Monitoring Station Communications, 3rd 	 49

Party Notification Verification, 3rd 	 57

Pass Keys 	 41

Passback Parking Operation, Anti 	 39

Passenger Dispatch Requirements, Elevator 	 33

Passive Communications Network Warranty 	 54

Password List 	 17, 56

Passwords, Camera 	 37

Patch Cords 	 54

Patch Panels 	 54

Pathways for Communications Cabling, Shared 	 34

Pathways, Fittings, Cables, Accessories, Conduits, 	 37

PDF Source Files, CAD 	 13

Pedestal for Gate Entrance Detail, Door Type T6 	 92

Pedestal, Card Reader 	 38

Penalties for Down Time 	 55

Penetration IT, Network Device Security 	 11

Penetration Requirements, Network 	 21

Penetration Testing 	 12

Per Function Basis Testing 	 18

Per Point Testing 	 18

Per System Component Testing 	 18

Per Total Entire System Testing 	 18

Performance Criteria 	 24

Performance Data 	 22

Performance of Work Warranty, Total 	 11, 17

Performance Requirements 	 55

Performance, Optimal 	 18

Performance, Substantial 	 50

Perimeter Door Reader 	 13

Perimeter Exit Single Door Detail, Door Type T3 
Emergency 	 89

Period, Warranty 	 17

Permits 	 56

Phone System, Intercom Integration with 	 8

Physical Electrical Environmental Requirements 	 22

Physical Protection of Parking Barrier 	 40

Picture Quality Affected by Camera Stability 	 25

PIN Assignment, Location Identifier 	 22

Pixels on Target 	 25

Plan Approval, Implementation 	 11

Plan for Alarm Points, Response 	 49

Plan, Architectural Floor 	 13

Plan, Test 	 56

Plate Recognition LPR North America, Licence 	 30

Plates, Power Supply Back 	 45

POD, Probability of Detection 	 24

POE Cameras, Power Over Ethernet 	29, 37

Point Installation Detail, Door Type T8 Tamper Point Monitoring 	 95

Point Monitoring Point Installation Detail, Door Type T8 Tamper 	 95

Point Schedule, Intrusion Detection 	 9, 16, 17, 22

Point Testing, Per 	 18

Point, Verification of Each 	 53

Point, Verification of Each Detection 	 53

Points, Addresses for Hardware Modules and 	 23

Points, Alarm 	 16, 17

Points, Contacts for Alarm 	 49

Points, Naming of Alarm 	 49

Points, Response Plan for Alarm 	 49

Ports, Communications Network 	 47

Power Communication Cable Separation 	 43

Power Controller, In Line 	 48

Power Failure Mode, Parking Barrier 	 39

Power Failure Operation 	 51

Power Failure, AC Restore, Power Restore, AC Fail, 	 14

Power Failure, Access Control Elevator 	 31

Power Injectors 	 37

Power Over Ethernet POE Cameras 	29, 37

Power Restore, AC Fail, Power Failure, AC Restore, 	 14

Power Supplies 	 9

Power Supply Back Plates 	 45

Power Supply Solutions 	 45

Power Supply UPS, Uninterruptible 	 21, 121

Power Transfer, Electrical 	 119

Practices, Best 	 6

Practices, Standards and 	 10

Practices, Wiring Best 	 46

Pre Qualified Security System Contractor 	 10

Pre Qualified Value Added Resellers and Installers 	 11

Pre-Approved Devices 	 23, 24

Pre-Approved Equipment 	 111

Pre-Approved Products 	 23

Pre-Approved Solutions 	 24

Precautions, Arc Flash 	 42

Pre-Commissioning Demonstration 	 19

Pre-Qualification, Request for 	 110

Prevention, Intrusion Deterrence 	 24

Prevention Through Environmental Design CPTED, Crime 	 26

Previous Updates, Verification of 	 23

Price, Modifications to Contract 	 11

Pricing of Contractor Work, Unit 	 46

Prior to Execution, Drawings 	 10

Prior to Incident, Recording 	 28

Privacy Laws Regarding Image Recording 	 29

Privacy Regulations, FIPPA 	 29

Privacy Regulations, MFIPPA 	 29

Probability of Detection POD 	 24

Problem Escalation Resolution 	 20

Procedure Documentation, Integration 	 19

Procedure, Equipment Substitution 	 96

Proceed, Notice to 	 15

Product Registration 	 56

Product Specifications 	 9

Product Specifications and Cut-Sheets 	 16, 17, 22

Products 	 23

Products Warranty, Defective 	 11

Products, Alternative 	 24

Products, Equipment Substitution 	 98

Products, Pre-Approved 	 23

Program Configure and Test 	 12

Program Evaluation, Training 	 21

Programmable Hardware 	 22

Programming Listings 	 23

Programming, Application 	 11

Programming, Database 	 11

Programming, Shift 	 57

Project Budget 	 24, 28

Project Documentation 	 56

Project Familiarity, Contractor Staff 	 20

Project Schedule 	 15

Project Specifications 	 6

Project Summary, Overall 	 61

Projects, Standards, Codes Applicable to Security 	 77

Proof Door Contacts, Explosion 	 119

Proof, Explosion 	 111

Proposed Testing and Acceptance Activities 	 16, 17, 22

Proprietary Communications Protocols 	 47

Proprietary Integration Licences 	 11

Protection Against Condensation 	 45

Protection of Parking Barrier, Physical 	 40

Protocols, Proprietary Communications 	 47

Provincial Standards 	 77

Proximity Card 	 118

Proximity Card Reader 	 52

Proximity Tag Credential, Long Range 	 118

PTZ Camera, Pan Tilt and Zoom 	 27, 123

Pull Boxes or Termination, Cable Slack for 	 43

Pull Boxes, Cable 	 43

Pulling Eyes 	 42

Pulling Length, Cable 	 43

Pulling Lubricant, Cable 	 43, 128

Pulling Tension, Cable 	 43

Push Button, Arming 	 120

Push Buttons, Exit 	 120

Push Paddle Door Release 	 40, 131

PVC Schedule 40 Conduit, Rigid 	 124

Q

Qualified Security System Contractor, Pre 	 10

Qualified Value Added Resellers and Installers, Pre 	 11

Quality Affected by Camera Stability, Picture 	 25

Quality Affected by Vibration, Image 	 25

Quality Assurance, Equipment Substitution 	 98

Quality Assurance, Testing and 	 18

Quality Control, Network Wiring Field 	 53

Quality Control, Security Wiring Field 	 53

Quantity of Bends 	 43

R

Raceway Conduit Alignment 	 43

Rack Module Assignment 	 22

Racks, Cable Trays and 	 43

Radius, Cable Bending 	 43

RAID Technology 	 28

Rail Mounted Terminal Blocks, DIN 	 46

Range Card Reader, Long 	 38, 118

Range Proximity Tag Credential, Long 	 118

Rate FAR, False Alarm 	 24

Rate, Frame 	 25, 26

Rating, CMR or CMP 	 37

Rating, Flame Test 	 46

Rating, FT-4 or FT-6 	 37

Reader Interface Unit 	 114

Reader Licences, Card 	 11

Reader Pedestal, Card 	 38

Reader Signals, Conditioning of Card 	 33

Reader, Arming Button Card 	 12

Reader, Disarming by Card 	 12

Reader, Elevator Card 	 30

Reader, Long Range Card 	 38, 118

Reader, Multi Technology 	 118

Reader, Perimeter Door 	 13

Reader, Proximity Card 	 52

Reading Equipment, Approved Credential and Credential 	 118

Real Time Status of Facility 	 14

Reason, Card Activities Access Granted Denied and 	 12

Recall, Elevator Fire 	 31, 34

Reception Areas 	 7

Rechargeable Lead Acid Batteries 	 119

Recognition LPR North America, Licence Plate 	 30

Recognition, Facial 	 29

Recognition, Image 	 25

Recognition, Johnson's Criteria for Detection Identification 	 25

Recommendation, Contractor Spare Parts 	 44

Recommendations, Manufacturer's Installation 	 45

Recorders NVR, Network Video 	 29

Recording Criteria, Video 	 28

Recording Devices, Industry Standard 	 29

Recording on Motion, Video 	 28

Recording Prior to Incident 	 28

Recording Requirements, Video 	 28

Recording Resolution, Video 	 28

Recording System API SDK, Video 	 30

Recording, Continuous Video 	 28

Recording, Privacy Laws Regarding Image 	 29

Recordings, Faithful and Reliable 	 28

Recordings, Searchable Video 	 29

Redundancy and Fail Over 	 28

Reference Documents 	 6

Reference Materials, Training 	 20

Regarding Image Recording, Privacy Laws 	 29

Region IT, Coordination with 	 12

Region Participation in Testing 	 57

Region Security System Architecture, Schematic of York 	 8

Region Security, WAN for York 	 8

Region Wide Alarm 	 57

Region, Changes Approval by York 	 10

Region, Consistent Functionality Across 	 11

Region, Demonstration to 	 18

Region, Written Authorisation from 	 11

Regional Access Levels 	 52

Regional Administration of System 	 20

Regional Approval of Updates 	 23

Regional Approved Commissioning Form 	 61

Regional Control Centre, Architecture of Sites Connected to Main 	 8

Regional Control Centre, Main 	 7

Regional Control System 	 7

Regional Facilities Distinct Icons 	 13

Regional Layout and Icons, Sample 	 139

Regional Security System 	 7

Regional Security System Naming Convention Standards 	 14

Regional Staff Training 	 20

Regional Standards Security, Operational, Information Technology, Meet All 	 11

Regional Support of System 	 20

Registration, Product 	 56

Regulations, FIPPA Privacy 	 29

Regulations, MFIPPA Privacy 	 29

Related Databases, Repopulating System 	 19

Relay, Door Interface 	 51

Relay, Interface 	 51

Release, Push Paddle Door 	 40, 131

Relevant Information Required for the Installation 	 16, 17, 22

Reliability, Video System 	 30

Reliable Recordings, Faithful and 	 28

Relocation of Equipment 	 46

Relocation of Equipment Location 	 45

Remote Monitoring 	 14

Repair Response Time 	 54

Repair Times, Monthly Incident 	 55

Repetition of Commissioning Tests 	 19

Repetition, Training 	 20

Replacement Components 	 54

Replacement Spare Parts 	 18

Repopulating System Related Databases 	 19

Report Existing Defects 	 44

Reporting, Elevator Destination 	 31

Reports, Trouble and Alarm 	 12

Request for Pre-Qualification 	 110

Request Form, Substitution 	 100

Request to Exit RTE Function 	 50

Request to Exit Sensors RTE REX 	 120

Required Conduits and Junction Boxes 	 21

Required for the Installation, Relevant Information 	 16, 17, 22

Requirement, Contractor Assistance 	 19

Requirement, Elevator Code Exit 	 31

Requirement, Fibre Backbone 	 36

Requirements for Parking Barrier, Civil Electrical Communications 	 40

Requirements Schedule, Maintenance 	 17

Requirements, Backup and Maintenance 	 23

Requirements, Electrical 	 9

Requirements, Elevator Passenger Dispatch 	 33

Requirements, Environmental 	 109

Requirements, General 	 6

Requirements, Grounding 	 48

Requirements, Handicapped Operator 	 51

Requirements, IP Address 	 47

Requirements, Labelling 	 56

Requirements, Network Penetration 	 21

Requirements, Parking Barrier Environmental 	 40

Requirements, Performance 	 55

Requirements, Physical Electrical Environmental 	 22

Requirements, SCADA 	 7

Requirements, Server Network Other IT 	 12

Requirements, Service Level 	 55

Requirements, Universal Washroom 	 41

Requirements, Up Time 	 55

Requirements, Video Recording 	 28

Resellers and Installers, Pre Qualified Value Added 	 11

Resellers, Access Control System Value Added 	 110

Reserved Addresses 	 9

Reset Vehicle Detection Loop, Activation, Entry and 	 39

Resets and Restarts, System 	 12

Resistance to Chemicals, Detection Loop 	 40

Resolution of Graphic Map, Image 	 13, 25

Resolution, Deficiency 	 16

Resolution, Image 	 25

Resolution, Problem Escalation 	 20

Resolution, Video Recording 	 28

Response Plan for Alarm Points 	 49

Response Time, Repair 	 54

Response Time, Service 	 18

Response Times, Incident 	 55

Responsibility and Subcontractors, Contractor 	 10

Responsibility for Errors, Contractor 	 23

Restarts, System Resets and 	 12

Restore, AC Fail, Power Failure, AC Restore, Power 	 14

Restore, Power Restore, AC Fail, Power Failure, AC 	 14

Restrictions, Arming 	 52

Restrictions, Elevator Code 	 30

Resubmission, Shop Drawing 	 23

Results Submission, Test 	 53, 56

Results, Cable Certification Test 	 53

Retesting After Adjustments 	 18

Return To Service Time 	 18

Review and Comment of Technical Shop Drawings 	 9

Review Arbiter, Final Submittal 	 15

Review, Shop Drawing 	 23

Revision History 	 2

REX, Request to Exit Sensors RTE 	 120

Rigid PVC Schedule 40 Conduit 	 124

Riser Diagrams, High Level 	 9

Riser Diagrams, System 	 9, 15, 21

Rodent Sealing of Conduits 	 43

Router 	 123

Routine Maintenance Training by Contractor 	 10

Routine Operation Training 	 19

Routing, Security Wiring 	 46

RTE REX, Request to Exit Sensors 	 120

RTE Function, Request to Exit 	 50

S

Safe Door Contacts, Intrinsically 	 119

Safe Elevator Control, Fail 	 33, 34

Safe, Intrinsically 	 111

Safety Alarms, Life 	 7

Safety Authority ESA, Electrical 	 42

Safety Code OESC, Ontario Electrical 	 37, 42, 124

Sample Graphic Alarm Map 	 139

Sample Regional Layout and Icons 	 139

SCADA Control Panel for ENV OMM 	 13, 49

SCADA Requirements 	 7

Scalable Architecture 	 7

Scenarios, Integration Techniques and Operational 	 16, 17, 22

Schedule 40 Conduit, Rigid PVC 	 124

Schedule Activation and Deactivation 	 12

Schedule Impact, Cost and 	 10

Schedule, Commissioning 	 16

Schedule, Device Landing 	 16

Schedule, Intrusion Detection Point 	 9, 16, 17, 22

Schedule, Maintenance Requirements 	 17

Schedule, Project 	 15

Schedule, Status Unlocked Tamper Faulted Active On 	 14

Schedule, Submission 	 16

Schedules, Time Zones, 	 14

Scheduling Elevator Access Control 	 34

Scheduling, Commissioning 	 19

Schematic of York Region Security System Architecture 	 8

Schematic(s) and Diagrams, Typical and Site-Specific Termination/Wiring 	 16, 21

Schematic(s) and Wiring Diagrams, System
Integration 	 16, 17, 22

Scope of Work 	 15

Scope, Training 	 20

Scripts, Software 	 17

SDK, Video Recording System API 	 30

Seal Filling Compound, Hazardous Area 	 124

Sealant, Conduit 	 128

Sealant, Fire 	 129

Sealing of Conduits, Rodent 	 43

Seamless Offline Operation 	 9

Search Bookmarking, Image 	 29

Search Criteria, Image 	 29

Searchable Video Recordings 	 29

Secondary Entrance Double Door Detail, Door Type T2 	 94

Secondary Entrance Single Door Detail, Door Type T2 	 88

Secondary Entry Single Door with Magnetic Lock Detail, 
Door Type T7 	 93

Section, Verification of Each 	 53

Secure Elevator Control, Fail 	 33, 34

Security Access Control and Intrusion Detection 	 23

Security Access Intrusion System Components 	 86

Security Applications, LAN for 	 34, 37

Security Assemblies, Typical Door 	 82

Security Components, Typical 	 82

Security Configurations, Standardised 	 23

Security Device Legend 	 62

Security Devices, Individual 	 61

Security Devices, Miscellaneous 	 119

Security Door Configurations, Standardised 	 82

Security Equipment, List of Approved 	 111

Security Installation Contractor 	 15

Security Operation, Local 	 7, 8

Security Penetration IT, Network Device 	 11

Security Projects, Standards, Codes Applicable to 	 77

Security Solution, Uniform 	 23

Security Staff Investigation 	 24

Security System Administrator 	 57

Security System Architecture, Schematic of York Region 	 8

Security System Armed 	 52

Security System Contractor, Pre Qualified 	 10

Security System Database Updates 	 11

Security System Device Summary 	 85

Security System Devices, Installation, 	 44

Security System Disarmed 	 52

Security System Effectiveness 	 24

Security System Functions and Operation, Confirmation of 	 50

Security System Installer 	 10

Security System Installer Comments and Concerns 	 9

Security System Naming Convention 	 60

Security System Naming Convention Standards, Regional 	 14

Security System Objectives 	 24

Security System Summary 	 62, 63

Security System, Installation and Configuration of 	 10

Security System, Integrated 	 7

Security System, Regional 	 7

Security System, Single 	 7

Security Terminology Definition, Standardised 	 65

Security Wiring Field Quality Control 	 53

Security Wiring Routing 	 46

Security, Operational, Information Technology, Meet All Regional Standards 	 11

Security, WAN for York Region 	 8

Segregation in Conduits, Cabling 	 21

Sensor Signal Wiring Testing 	 53

Sensor, Verification of Each 	 53

Sensors HFS, Bond 	 47

Sensors HFS, Hold Force 	 47

Sensors RTE REX, Request to Exit 	 120

Separation, Maintain Fire 	 43

Separation, Power Communication Cable 	 43

Sequence of Operation ADO 	 51

Sequence of Operation, Explanation of the 	 16, 17, 22

Sequencer Board 	 51

Sequencing, Operational 	 53

Sequential Addresses Starting from 	 9

Serial Numbers 	 17, 56

Server Network Other IT Requirements 	 12

Server, Database 	 21

Service Level Requirements 	 55

Service Levels, Target 	 54

Service Mode, Elevator 	 33

Service Response Time 	 18

Service Station Communications, Off Site Monitoring 	 49

Service Station, Off Site Monitoring 	 13, 42

Service Time, Return To 	 18

Services, Health 	 7

Services, Information Technology 	 12, 21

Services, Judicial 	 7

Services, Social 	 7

Settings Addresses, Switch 	 23

Settings, Hardware DIP Switch 	 9

Shadows, Illumination and 	 26

Shaky Images 	 25

Shared Pathways for Communications Cabling 	 34

Sheets, Cut 	 9

Sheets, Data 	 16, 17

Shift Programming 	 57

Shop Drawing Resubmission 	 23

Shop Drawing Review 	 23

Shop Drawings 	 21

Shop Drawings, Review and Comment of Technical 	 9

Shop Drawings, Technical 	 9, 15

Signal Wiring Testing, Sensor 	 53

Signals, Conditioning of Card Reader 	 33

Signature, Digital Image 	 29

Simple Apparatus 	 111

Simulation Software, Camera 	 27

Single Door Detail, Door Type T1 Arming Disarming 	 87

Single Door Detail, Door Type T2 Secondary Entrance 	 88

Single Door Detail, Door Type T3 Emergency 
Perimeter Exit 	 89

Single Door with Magnetic Lock Detail, Door Type T7 Secondary Entry 	 93

Single Security System 	 7

Single User Interface 	 7

Site Listing 	 60

Site Specific Device Termination Diagrams, Typical and 	 9

Site Testing 	 56

Site, Audit Trail Log for Entire 	 12, 13

Site, Custom Alarms for Each 	 13

Sites Connected to Main Regional Control Centre, 
Architecture of 	 8

Sites, Locations and 	 12

Site-Specific Termination/Wiring Schematic(s) and 
Diagrams, Typical and 	 16, 21

Size, Training Class 	 20

Slack for Pull Boxes or Termination, Cable 	 43

Smart Pac 	 48

Snubbing Diodes 	 48

Social Services 	 7

Software and Firmware Versions 	 23

Software Client Application, Alarm Monitoring 	 13

Software Client, Alarm Monitoring 	 12

Software Integration, Installation Enterprise 	 50

Software Licencing 	 11

Software Scripts 	 17

Software System Configuration 	 11

Software Update Compatibility, Firmware 	 14

Software, Camera Emulation 	 27

Software, Camera Modelling 	 27

Software, Camera Simulation 	 27

Software, Installation 	 56

Solution, Uniform Security 	 23

Solutions, Cabinet, Panel 	 45

Solutions, Enclosure 	 45

Solutions, Power Supply 	 45

Solutions, Pre-Approved 	 24

Source Files, CAD PDF 	 13

Sources, Illumination Lighting 	 27

Space, Wall 	 9

Spare Cabinet Capacity 	 45

Spare Enclosure Capacity 	 45

Spare Input and Output Capacity 	 44

Spare Parts 	 56

Spare Parts Recommendation, Contractor 	 44

Spare Parts, Replacement 	 18

Special Tools 	 56

Specific Device Termination Diagrams, Typical and Site 	 9

Specifications 	 6

Specifications and Cut-Sheets, Product 	 16, 17, 22

Specifications, Architectural 	 41

Specifications, Cabinet 	 44

Specifications, Compliance with 	 10

Specifications, Enclosure 	 44

Specifications, Improvements to 	 6

Specifications, Overview of 	 7

Specifications, Product 	 9

Specifications, Project 	 6

Splice Locations 	 44, 46

Stability of Camera 	 25

Stability, Picture Quality Affected by Camera 	 25

Staff Investigation, Security 	 24

Staff Project Familiarity, Contractor 	 20

Staff Training, Regional 	 20

Stand Alone Operation 	 51

Standalone Systems 	 7

Standard Recording Devices, Industry 	 29

Standard, Adherence to Labelling 	 136, 137

Standard, York ITS Cable and Wiring 	 34

Standardised Abbreviations 	 103

Standardised Acronyms 	 103

Standardised Security Configurations 	 23

Standardised Security Door Configurations 	 82

Standardised Security Terminology Definition 	 65

Standards 	 6

Standards and Practices 	 10

Standards Security, Operational, Information Technology, Meet All Regional 	 11

Standards, Applicable 	 11

Standards, Codes Applicable to Security Projects 	 77

Standards, Documentation 	 81

Standards, Internal 	 77

Standards, International 	 77

Standards, Municipal 	 77

Standards, National 	 77

Standards, Provincial 	 77

Standards, Regional Security System Naming Convention 	 14

Standards, Technology 	 77

Starting from, Sequential Addresses 	 9

Station Communications, 3rd Party Monitoring 	 49

Station Communications, Off Site Monitoring Service 	 49

Station Notification, Testing Monitoring 	 50

Station, Central Monitoring 	 21

Station, Off Site Monitoring Service 	 13, 42

Status Armed Disarmed Normal Alarmed Forced 
Held Open 	 13, 14

Status Disposition, Associated 	 13

Status Normal Alarmed Forced Held Open Locked 	 14

Status of Facility, Real Time 	 14

Status Offline AC Fail Battery Trouble 	 14

Status Panel 	 14

Status Unlocked Tamper Faulted Active On Schedule 	 14

Streamers, Camera 	 27

Streamers, Video 	 123

Strike Failure Modes, Electric 	 48

Strikes, Electric Door 	 48, 119

Style, Submittal Format and 	 15

Subcontractors, Contractor Responsibility and 	 10

Subcontractors, Locksmith 	 10

Submission for Approval, Training Syllabus 	 20

Submission Schedule 	 16

Submission, Test Results 	 53, 56

Submissions, Documentation 	 9, 81

Submittal Format and Style 	 15

Submittal Review Arbiter, Final 	 15

Submittal Virus Checking Malware 	 15

Submittals 	 15

Substantial Performance 	 50

Substitution Approval, Equipment 	 24

Substitution Procedure, Equipment 	 96

Substitution Products, Equipment 	 98

Substitution Quality Assurance, Equipment 	 98

Substitution Request Form 	 100

Summary, Overall Project 	 61

Summary, Security System 	 62, 63

Summary, Security System Device 	 85

Sunlight Impact on Camera Imaging, Direct 	 26

Supervision, End Of Line EOL 	 46

Supplied Applications, Manufacturer 	 12

Supplies, Power 	 9

Supplies, Training 	 20

Supply Back Plates, Power 	 45

Supply Solutions, Power 	 45

Supply UPS, Uninterruptible Power 	 21, 121

Support of System, Regional 	 20

Supports, Catenary 	 43

Suppression of Induced Back EMF 	 48

Surplus Equipment, Decommissioned 	 47

Surveillance Cameras 	 24

Surveillance Cameras, 360° 	 27

Surveillance Closed Circuit Television 	 24

Surveillance Commissioning, CCTV 	 64

Surveillance System, Video 	 61

Survival Criteria, Operating and 	 109

Switch and Hardware Configurations, DIP 	 16, 21, 22

Switch for Elevator Access Control, Bypass 	 34

Switch Settings Addresses 	 23

Switch Settings, Hardware DIP 	 9

Switch, Layer 3 Capable 	 37, 123

Switch, Wireless Modem and Network 	 21, 47

Switches, Jumpers and 	 23

Switches, Network 	 12

Syllabus Approval, Training 	 20

Syllabus Submission for Approval, Training 	 20

System Administration Manuals 	 17

System Administrator, Security 	 57

System Administrators 	 14

System Alarm Monitor, Access Control 	 13

System Analyst, Business 	 21

System API SDK, Video Recording 	 30

System Architecture, Schematic of York Region Security 	 8

System Armed, Security 	 52

System Availability, Overall 	 54

System Capability without Central Database 	 51

System CCTV, Closed Circuit Television 	 123

System Component Testing, Per 	 18

System Components, Intrusion Detection 	 113

System Components, Security Access Intrusion 	 86

System Configuration, Software 	 11

System Contractor, Fire Alarm 	 47

System Contractor, Pre Qualified Security 	 10

System Controllers and Panels 	 60

System Database Updates, Security 	 11

System Deployment and Configuration 	 12

System Device Summary, Security 	 85

System Devices, Installation, Security 	 44

System Digital Video Management, CCTV 	 9

System Disarmed, Security 	 52

System DVMS, Digital Video Management 	 24, 122, 123

System Effectiveness, Security 	 24

System Equipment Licencing Hardware 	 10

System Failure 	 55

System Functions and Operation, Confirmation of Security 	 50

System Installer Comments and Concerns, Security 	 9

System Installer, Security 	 10

System Integration Schematic(s) and Wiring 
Diagrams 	 16, 17, 22

System Integration Wiring Diagrams 	 9

System Keypad Display, Intrusion Detection 	 12

System Layout Floorplan 	 15, 21

System Naming Convention Standards, Regional Security 	 14

System Naming Convention, Security 	 60

System Objectives, Security 	 24

System Operators 	 7

System Operators Documentation 	 17

System Related Databases, Repopulating 	 19

System Reliability, Video 	 30

System Resets and Restarts 	 12

System Riser Diagrams 	 9, 15, 21

System Summary, Security 	 62, 63

System Testing, Per Total Entire 	 18

System User Interface, Access Control 	 9

System Value Added Resellers, Access Control 	 110

System, Installation and Configuration of Security 	 10

System, Integrated Security 	 7

System, Integration of Facility into Existing 	 50

System, Intercom Integration with Phone 	 8

System, Intrusion Detection 	 7

System, Live 	 21

System, Regional Administration of 	 20

System, Regional Control 	 7

System, Regional Security 	 7

System, Regional Support of 	 20

System, Single Security 	 7

System, Verification of Complete 	 53

System, Video Surveillance 	 61

Systems, Independent 	 7

Systems, Standalone 	 7

T

T1 Arming Disarming Single Door Detail, Door Type 	 87

T2 Secondary Entrance Double Door Detail, Door Type 	 94

T2 Secondary Entrance Single Door Detail, Door Type 	 88

T3 Emergency Perimeter Exit Single Door Detail, 
Door Type 	 89

T4 Overhead Garage Door Detail, Door Type 	 90

T5 Overhead Garage Door with Access Control Detail, 
Door Type 	 91

T6 Pedestal for Gate Entrance Detail, Door Type 	 92

T7 Secondary Entry Single Door with Magnetic 
Lock Detail, Door Type 	 93

T8 Tamper Point Monitoring Point Installation Detail, 
Door Type 	 95

Table of Contents 	 3

Tag Assignments, Module 	 22

Tag Credential, Long Range Proximity 	 118

Tag Numbers, Field 	 22

Tamper Faulted Active On Schedule, Status Unlocked 	 14

Tamper Point Monitoring Point Installation Detail, 
Door Type T8 	 95

Tamper, Enclosure 	 14

Tape, Electrical Insulating 	 128

Target Intruder 	 25

Target Service Levels 	 54

Target, Pixels on 	 25

TCP/IP Coordination, Network 	 21

Technical Clarifications 	 9

Technical Design 	 9

Technical Documentation 	 15

Technical Manuals 	 17

Technical Notes 	 17

Technical Shop Drawings 	 9, 15

Technical Shop Drawings, Review and Comment of 	 9

Technicians, Factory Trained 	 6

Techniques and Operational Scenarios, Integration 	 16, 17, 22

Technology Reader, Multi 	 118

Technology Services, Information 	 12, 21

Technology Standards 	 77

Technology, Meet All Regional Standards Security, Operational, Information 	 11

Technology, RAID 	 28

Telecommunications Ground 	 48

Television System CCTV, Closed Circuit 	 123

Television, Surveillance Closed Circuit 	 24

Temperature, Ambient Air 	 109

Temperature, Operating 	 109

Temporary Configurations 	 56

Temporary Construction Cylinders 	 40

Temporary Lock Cylinders, Construction 	 131

Tenant Elevator Access Control, Multi 	 34

Tension, Cable Pulling 	 43

Terminal Blocks 	 128

Terminal Blocks, DIN Rail Mounted 	 46

Terminal Numbers 	 22

Termination Connection, TIA-568A 	 36

Termination Diagrams, Typical and Site Specific Device 	 9

Termination, Cable Slack for Pull Boxes or 	 43

Termination, Contract 	 24

Termination/Wiring Schematic(s) and Diagrams, 
Typical and Site-Specific 	 16, 21

Terminations, Field Wiring 	 128

Terminology Definition, Standardised Security 	 65

Test Alarm 	 49

Test and Verify, Document 	 18

Test Plan 	 56

Test Rating, Flame 	 46

Test Results Submission 	 53, 56

Test Results, Cable Certification 	 53

Test, Program Configure and 	 12

Tester, Calibrated Wiring 	 53

Testing and Acceptance Activities, Proposed 	 16, 17, 22

Testing and Commissioning 	 10

Testing and Quality Assurance 	 18

Testing Monitoring Station Notification 	 50

Testing, Cost of 	 12

Testing, Exterior Facility Door 	 57

Testing, Final Acceptance 	 18

Testing, Mechanical and Electronic Door 	 57

Testing, Penetration 	 12

Testing, Per Function Basis 	 18

Testing, Per Point 	 18

Testing, Per System Component 	 18

Testing, Per Total Entire System 	 18

Testing, Region Participation in 	 57

Testing, Sensor Signal Wiring 	 53

Testing, Site 	 56

Tests for Device Functionality, Functional 	 53

Tests, Repetition of Commissioning 	 19

Theory of Operation 	 17

Thermal Cameras 	 26

TIA-568A Termination Connection 	 36

Tie Wraps, Velcro 	 43

Ties, Cable 	 128

Tilt and Zoom PTZ Camera, Pan 	 27, 123

Time in ISO Format, Local Date and 	 12

Time Requirements, Up 	 55

Time Status of Facility, Real 	 14

Time Zones, Schedules 	 14

Time, Cumulative Down 	 55

Time, Exit Delay 	 13

Time, Penalties for Down 	 55

Time, Repair Response 	 54

Time, Return To Service 	 18

Time, Service Response 	 18

Timer, Countdown 	 52

Times, Incident Response 	 55

Times, Monthly Incident Repair 	 55

Title Block, Drawing 	 82, 84

Tools, Special 	 56

Total Entire System Testing, Per 	 18

Total Performance of Work Warranty 	 11, 17

Trail Log for Entire Site, Audit 	 12, 13

Trail Log Verification, Audit 	 57

Trained Installers, Factory 	 6

Trained Technicians, Factory 	 6

Training 	 19

Training Audience 	 20

Training by Contractor, Routine Maintenance 	 10

Training Class Size 	 20

Training Duration 	 20

Training in English 	 20

Training Location 	 20

Training Program Evaluation 	 21

Training Reference Materials 	 20

Training Repetition 	 20

Training Scope 	 20

Training Supplies 	 20

Training Syllabus Approval 	 20

Training Syllabus Submission for Approval 	 20

Training, Maintenance 	 19

Training, Regional Staff 	 20

Training, Routine Operation 	 19

Transfer Mode ATM, Asynchronous 	 36

Transfer, Electrical Power 	 119

Transformer Installation 	 47

Transformer, Control 	 120

Transmission to Mobile Device, Image 	 29

Travelling Cable, Elevator 	 31, 33

Trays and Racks, Cable 	 43

Trouble Alarms, Arming 	 12

Trouble and Alarm Reports 	 12

Trouble, Backup, Battery 	 14

Trouble, Status Offline AC Fail Battery 	 14

Tub Enclosure Layout Diagrams 	 9, 16, 17, 22

Twisted Pair UTP, Category 6 Unshielded 	 123

Twisted Pair UTP, Unshielded 	 36

Type T1 Arming Disarming Single Door Detail, Door 	 87

Type T2 Secondary Entrance Double Door Detail, Door 	 94

Type T2 Secondary Entrance Single Door Detail, Door 	 88

Type T3 Emergency Perimeter Exit Single Door Detail, 
Door 	 89

Type T4 Overhead Garage Door Detail, Door 	 90

Type T5 Overhead Garage Door with Access Control 
Detail, Door 	 91

Type T6 Pedestal for Gate Entrance Detail, Door 	 92

Type T7 Secondary Entry Single Door with Magnetic 
Lock Detail, Door 	 93

Type T8 Tamper Point Monitoring Point Installation 
Detail, Door 	 95

Types to be Monitored Off-Site, Alarm 	 49

Types, Approved Cabling 	 126

Types, Wire 	 42

Typical and Site Specific Device Termination Diagrams 	 9

Typical and Site-Specific Termination/Wiring 
Schematic(s) and Diagrams 	 16, 21

Typical Door Security Assemblies 	 82

Typical Security Components 	 82

U

Uniform Security Solution 	 23

Uninterruptible Power Supply UPS 	 21, 121

Unique Name 	 60

Unit Cameras, Multi 	 27

Unit Pricing of Contractor Work 	 46

Unit, Reader Interface 	 114

Units, Calibration 	 56

Universal Washroom 	 132

Universal Washroom Alarm Monitoring 	 42

Universal Washroom Requirements 	 41

Unlimited Number of Cameras 	 122

Unlocked Tamper Faulted Active On Schedule, Status 	 14

Unshielded Twisted Pair UTP 	 36

Unshielded Twisted Pair UTP, Category 6 	 123

Up Time Requirements 	 55

Update Compatibility, Firmware Software 	 14

Update Graphical Map 	 13

Updates, Regional Approval of 	 23

Updates, Security System Database 	 11

Updates, Verification of Previous 	 23

Upgrade Camera Firmware Approval 	 28

Upgrades, DVMS 	 28

Upgrades, Lighting 	 29

UPS, Uninterruptible Power Supply 	 21, 121

User Interface, Access Control System 	 9

User Interface, Graphical 	 13

User Interface, Single 	 7

User Manuals 	 56

UTP, Category 6 	 36

UTP, Category 6 Unshielded Twisted Pair 	 123

UTP, Unshielded Twisted Pair 	 36

V

Value Added Resellers and Installers, Pre Qualified 	 11

Value Added Resellers, Access Control System 	 110

Vehicle Detection Loop Amplifiers 	 40, 130

Vehicle Detection Loop, Activation, Entry and Reset 	 39

Vehicle Detection Loops 	 38, 40

Vehicle Detector Loops 	 130

Vehicle Parking Departure Loop 	 39

Velcro Tie Wraps 	 43

Ventilation, Cabinet, Panel 	 45

Ventilation, Enclosure 	 45

Verification of Complete System 	 53

Verification of Each Area 	 53

Verification of Each Detection Point 	 53

Verification of Each Point 	 53

Verification of Each Section 	 53

Verification of Each Sensor 	 53

Verification of Previous Updates 	 23

Verification, 3rd Party Notification 	 57

Verification, Audit Trail Log 	 57

Verify, Document Test and 	 18

Version, Firmware 	 16

Versions, Software and Firmware 	 23

Vertical and Horizontal Wiring Diagrams 	 9, 15, 21

Vibration of Camera 	 25

Vibration, Image Quality Affected by 	 25

Video Cabling, Network and 	 34, 123

Video Compression 	 28

Video Image Archiving 	 29

Video Integration with Access Control 	 28

Video Management System DVMS, Digital 	 24, 122, 123

Video Management, CCTV System Digital 	 9

Video Recorders NVR, Network 	 29

Video Recording Criteria 	 28

Video Recording on Motion 	 28

Video Recording Requirements 	 28

Video Recording Resolution 	 28

Video Recording System API SDK 	 30

Video Recording, Continuous 	 28

Video Recordings, Searchable 	 29

Video Streamers 	 123

Video Surveillance System 	 61

Video System Reliability 	 30

Virtual LAN VLAN 	 37

Virus and Malware Avoidance Certification 	 9

Virus Checking Malware, Submittal 	 15

Visitor Management 	 20

VLAN 	 123

VLAN, Virtual LAN 	 37

W

Wall Space 	 9

WAN for York Region Security 	 8

WAN, Wide Area Network 	 21

Warning Labels 	 134

Warranty 	 54

Warranty Assignment 	 56

Warranty Contact Information 	 49, 134

Warranty Criteria, Lifetime Cabling 	 54

Warranty Details 	 16

Warranty Period 	 17

Warranty, Defective Products 	 11

Warranty, Network Cable 	 54

Warranty, Passive Communications Network 	 54

Warranty, Total Performance of Work 	 11, 17

Washroom Alarm Monitoring, Universal 	 42

Washroom Kit, Available 	 132

Washroom Kits, Code Compliant 	 42

Washroom Requirements, Universal 	 41

Washroom, Barrier Free 	 41

Washroom, Universal 	 132

Waste and Wastewater Control Panel Outputs 	 47

Wastewater Control Panel Outputs, Waste and 	 47

Waterproofing, Moisture and 	 128

Watertight Cable Connectors 	 43

Wide Alarm, Facility 	 57

Wide Alarm, Region 	 57

Wide Area Network WAN 	 21

Wire and Cable Markers Labels 	 128

Wire Numbers 	 22

Wire Types 	 42

Wired Buttons 	 7

Wireless Alarm Notification 	 49

Wireless Buttons 	 7

Wireless Modem and Network Switch 	 21, 47

Wires and Cables, Installation of 	 42

Wiring Accessories 	 128

Wiring and Miscellaneous Accessories 	 126

Wiring Best Practices 	 46

Wiring Certification, Network 	 53

Wiring Continuous, Feeder 	 44

Wiring Details 	 22

Wiring Diagrams, Electrical Connections and 	 16, 17, 22

Wiring Diagrams, System Integration 	 9

Wiring Diagrams, System Integration 
Schematic(s) and 	 16, 17, 22

Wiring Diagrams, Vertical and Horizontal 	 9, 15, 21

Wiring Field Quality Control, Network 	 53

Wiring Field Quality Control, Security 	 53

Wiring Identification 	 56

Wiring Labelling 	 56

Wiring List 	 46

Wiring Routing, Security 	 46

Wiring Standard, York ITS Cable and 	 34

Wiring Terminations, Field 	 128

Wiring Tester, Calibrated 	 53

Wiring Testing, Sensor Signal 	 53

Without Central Database, System Capability 	 51

Work Warranty, Total Performance of 	 11, 17

Work, Execution of Construction 	 42

Work, Scope of 	 15

Work, Unit Pricing of Contractor 	 46

Working Drawings to Authority Having Jurisdiction 	 10

Working, Hot Circuit 	 42

Workstation Licences 	 11

Wraps, Velcro Tie 	 43

Written Authorisation from Region 	 11

Written Confirmation of Functionality 	 18

Y

York ITS Cable and Wiring Standard 	 34

York Region Security System Architecture, Schematic of 	 8

York Region Security, WAN for 	 8

York Region, Changes Approval by 	 10

Z

Zipstream, Camera CODEC, JPEG, MJPEG, H.264, H.265, 	 28

Zones, Monitor 	 14

Zones, Schedules, Time 	 14

Zoom PTZ Camera, Pan Tilt and 	 27, 123